## Functions (2)
FUNCTION | Option | EQUIPMENT | Sizing Parameters | Technical solution | Price on ESS | Options | Comments
UTILITIES
To protect againt taconis |  | volume
To provide air instrument | X | Air compressors |  |  |  |  | Very rare (JT60SA)
To remove heat (Turbines, compressors, pumps) |  | Water
To remove heat |  | Air
To precool |  | LN2
To regenerate dryer. To condition Dryer, ORS, Adsorbers |  | GN2
To provide power to rotating equipments, heaters and control |  | Electricity
To condition and start unit |  | Helium
TO CONDITION WCS, ORS, WARM STORAGES
To pressurize / depressurize
To perform cooling down of system / Customer
To perform warming up of system / Customer |  | Heaters |  |  |  |  | immersed HX, on-line, external …
To pressurize / set pressure
To get pure helium in the system and verify helium quality |  | Vacuum pumps + dedicated piping + manual valves to pressurize/depressuriez
TO CONDITION
To pressurize / depressurize the system and subsytem |  | by-pass valve of main interface valve.
To perform cooling down of system / Customer
To perform warming up of system / Customer |  | Heaters |  |  |  |  | immersed HX, on-line, external …
To pressurize / set pressure
To get pure helium in the system and verify helium quality |  | Vacuum pumps + dedicated piping + manual valves to pressurize/depressuriez
TO STORE GAS
To store Warm Helium | X | GHe Buffers | Volume & Pressure | Carbone steel + rustol |  |  | Necessary all the time, but could be supplied by customer
To store cold helium produced | X | Lhe Storage | Volume & Pressure | Dewar
To provide cold nitrogen to the plant. | X | LN2 Storage | Volume & Pressure | LN2 + Thermosiphon.
TO COMPRESS
To compress helium |  | VLP, LP, HP | HP outlet pressure, flow, regulation (API)
To adjusts pressure |  | Gas Management Panel
To adjust compressor capacity / power consumption |  | VFD / Slide valves / Pressure regulation | VFD
To lubricate, remove heat, insulate |  | Oil | multiple supplier / oil compatibility
To remove Heat from oil, helium , motors with water or fan |  | Oil and Helium coolers | delta T max --> flow
To recover hot power | X | Heat Recovery System
To remove liquid oil from compressors outlet to 10 ppm |  | First Coalescer stage in oil separator tank | retention time (2 min) first stage coalescer
To remove vapour oil from compressors outlet |  | Charcoal Towers | Volumetric flow (= gas speed & aerosol quantity ?)
To remove water |  | Dryer + Regeneration Heater + GN2
To interconnect skids |  | Interfaces valves on CB
TO REMOVE OIL TO ppb level ATER COMPRESSOR (10ppm outlet)
To remove liquid oil from compressors outlet |  | Coalescers filters | Oil inlet level( max 20 ppm all the time ?), Volumetric flow (gas speed)
To send back oil to compressor |  | LS + auto valve | distance ORS / compressor
To detect if oil in last coalescer | X | LS
To detect pressure drop evolution for each stage | X | DP on each coalescer
To see oil | X | Visual indicator | OPTION
To remove vapour oil from compressors outlet |  | Charcoal Towers | Volumetric flow (= gas speed & aerosol quantity ?)
To circulate on chacoal adsorber with warm N2 to remove water |  | Regeneration circuit
To provide power to warm Nitrogen with integrated system | X | Integrated electrical Heater (mobile in standard solution)
To remove water on helium feed |  | Dryer + Regeneration Heater + GN2 inlet
To interconnect skids |  | Interfaces valves on CB
TO OBTAIN GOOD THERMAL INSULATION
Insulate thermally > 80K |  | Vacuum Vessels under vacuum or perlite
Insulate thermally < 80K |  | Vacuum Vessels under vacuum
To remove air from vessel |  | Vacuum group
To limit radiation |  | MLI + vacuum
To limit conduction of supports |  | fiberglass, support from top ?
TO PRODUCE COLD HELIUM
Produce 80K | X | HX + Turbines or 2HX + 1 phase separator |  |  |  |  | Need LN2 Supply (mainly a customer request)
Produce 30K/50K for TS | * | Turbines
Produce 4,5K Liquid |  | Turbines + JT or Liquid Turbine
To recover frigories from customer return |  | Different valves on return
TO REMOVE IMPURITIES FROM HELIUM
To trap air impurities
To trap Neon & H2 (swith in option) | *
To dry initially the adsorbers |  | Design all circuit for hot temperature
To regenerate adsorbers |  | Warming up with heater or atm vaporizers
To condition adsorbers automaticaly | * | Vacuum pumps + HP to pressurize
To measure presence of air. N2 leak cross HX/ Saturation of 80K adsorbers |  | N2 analyzer in WCS & RCB
To measure presence of air / Saturation of 80K adsorbers | X | O2 analyzer
To monitor saturation of 20K adsorbers | X | H2 analyzer / NE Analyzer
TO PRODUCE HELIUM BELOW 4,5K
To get sub atm pressure with cold rotating equipment |  | Cold compressor
To get sub atm pressure with warm rotating equipment |  | Warm Compressor / Vacuum pumps
To protect against air ingress if sub-atm |  | Helium Guard
VALVES & INSTRUM
To isolate & control |  | Cryovalves
To avoid cloaging turbines and exchangers |  | Filters
to monitor (Temp, Level, Pressure) |  | Instrum
Provide high cryogenic flow to users | X | Cold circulator
Simulate loads | X | Heaters |  |  |  |  | immersed HX, on-line, external …
To provide cryogenic fluid at different temperature with low heat losses | X | Multi Lines
To monitor pressure |  | Pressure
To monitor level |  | Supra conductor level
To detect presence of fluid (oil) or lack of fluid (water) |  | Level switch
To measure temperature and perform performances calculation |  | Cryogenic Temeprature Probe
To monitor oil presence at ORS outlet | * | CnHm |  |  |  |  | Requested most of the time
MECHANICAL
To get good line flexibility |  | low thickness piping class , elbows …
To resist agains pressure |  | Mechanical calculated.
ELECTRICAL SYSTEM
To distribute LV Power |  | Electrical cabinet
CONTROL SYSTEM
To control automatically the process |  | DCS
To provide interface to operator for control |  | HMI
To interconnect instrumentation signals |  | Electrical cabinet
SAFETY
To protect system agains over pressure | X | PSV
To detect PSV leakage | X
To collect PSV | X | PSV collector / ambiance analyzer
RECOVER IMPURE HELIUM
To recover low pressure impure helium and store it at low pressure | X | Gas Bag
To compress helium ( at high pressure most of the time) | X | Recovery compressors
To store impure helium | X | Impure storage
To purify helium and inject back to the cycle. | X | purifier
GENERAL
Minimize impact on design with change of regulation.
Installation : minimize time | X
Start-up : minimize time