## Summary
[14 empty] | S | M | L
[9 empty] | LP |  |  | HP |  | MYCOM internal Volume ratio | [7 empty] | BVR | 2.2 | 2.6 |  | BVR | 2.6 | 2.6
[9 empty] | 1.6 |  |  |  |  | BEST MP Pressure |  |  | BEST HP Pressure |  |  |  |  | Pinlet | 1.05 | 3.7074 |  | Pinlet | 1.01 | 4.6589
[8 empty] | Pin | 1.05 |  |  | 5.4 |  | Vi | Vi | Vi | Vi | Vi | Vi |  |  | Ideal Poutlet | 3.7074 | 17.1011 |  | Ideal Poutlet | 4.6589 | 17.1011
[8 empty] | Tin | 323 |  |  | 313 |  | 2.63 | 3.65 | 5.8 | 2.63 | 3.65 | 5.8 |  |  | Pr | 3.5308 | 4.6127 |  | Pr | 4.6127 | 3.6707
|  | air molar mass | 28.9586 |  |  |  |  | rho | 0.15648 |  |  | 0.83046 |  | 4.9331 | 8.3341 | 17.4853 | 25.3701 | 42.861 | 89.9246
|  | air density | 1.2758 |  |  |  |  | Pout | 5.4 |  |  | 27 |  | 4.6982 | [8 empty] | 3.5 | 3.5 |  |  | 3.5 | 3.5
[8 empty] | Isotherm eff. | 54.8% |  |  | 59.3% | [10 empty] | 3.675 | 12.8625 |  |  | 3.535 | 12.3725
[8 empty] | Ideal Vi | 2.7829 |  | Ideal Vi | 2.6367 |  | 1.05 | 3.675 | 12.8625 |  |  |  | L | 2.63
[9 empty] | 5.1429 |  |  | 5 |  | 2 | 7 | 24.5 |  |  |  | M | 3.65 |  |  |  | 1.1 | 3.85 | 13.475
|  |  |  | 59.1667 | 49 | 60 |  | 59 | [11 empty] | H | 5.8 |  |  |  | 1.05
|  | MANUFACTURER | MODEL | 3550 | 2940 | 3550 | Vol % | 3540 | LP Flow | LP Power |  | HP Flow | HP Power | [11 empty] | 7
MYCOM-125SUD 237,329577464789 m3/h |  | MYCOM | 125SUD | 140 | 197.1042 | 238 | 79% | 237.3296 | 10.3159 | 20.6962 |  | 54.7483 | 96.6684 | [11 empty] | 6.6667
MYCOM-200 VSD 973,250704225352 m3/h |  | MYCOM | 200 VSD | 574 | 808.293 | 976 | 79% | 973.2507 | 42.3039 | 84.8717 |  | 224.514 | 396.4216
MYCOM-200 VMD 1217,56056338028 m3/h |  | MYCOM | 200 VMD | 718 | 1011.1944 | 1221 | 79% | 1217.5606 | 52.9233 | 106.1766 |  | 280.8725 | 495.9331
MYCOM-200 VLD 1456,88450704225 m3/h |  | MYCOM | 200 VLD | 859 | 1209.9549 | 1461 | 79% | 1456.8845 | 63.3259 | 127.0467 |  | 336.0809 | 593.4139
MYCOM-250 VSD 1898,63661971831 m3/h |  | MYCOM | 250 VSD | 1120 | 1576.8338 | 1904 | 79% | 1898.6366 | 82.5273 | 165.5694 |  | 437.9863 | 773.347
MYCOM-250 VMD 2373,29577464789 m3/h |  | MYCOM | 250 VMD | 1400 | 1971.0423 | 2380 | 79% | 2373.2958 | 103.1592 | 206.9617 |  | 547.4829 | 966.6838
MYCOM-250 VLD 2832 m3/h |  | MYCOM | 250 VLD | 1670 | 2352 | 2840 | 79% | 2832 | 123.0975 | 246.9627 |  | 653.2989 | 1153.5218
MYCOM-250 VLLD 3357,51549295775 m3/h |  | MYCOM | 250 VLLD | 1980 | 2788.4451 | 3367 | 79% | 3357.5155 | 145.9399 | 292.79 |  | 774.5272 | 1367.5732
MYCOM-320 VSD 3815,22253521127 m3/h |  | MYCOM | 320 VSD | 2250 | 3168.5746 | 3826 | 79% | 3815.2225 | 165.8349 | 332.704 |  | 880.1132 | 1554.0051
MYCOM-320 VMD 4747,58873239437 m3/h |  | MYCOM | 320 VMD | 2800 | 3942.9127 | 4761 | 79% | 4747.5887 | 206.3617 | 414.0104 |  | 1095.1958 | 1933.7737
MYCOM-320 VLD 5679,95492957747 m3/h |  | MYCOM | 320 VLD | 3350 | 4717.2507 | 5696 | 79% | 5679.9549 | 246.8885 | 495.3168 |  | 1310.2783 | 2313.5423
MYCOM-400SUD 7782,01690140845 m3/h |  | MYCOM | 400SUD | 4590 | 6463.031 | 7804 | 79% | 7782.0169 | 338.2581 | 678.6258 |  | 1795.1917 | 3169.748
MYCOM-400MUD 9664,6985915493 m3/h |  | MYCOM | 400MUD | 5760 | 8026.6141 | 9692 | 79% | 9664.6986 | 420.0919 | 842.8038 |  | 2229.4974 | 3936.5963
MYCOM-400LUD 11682 m3/h |  | MYCOM | 400LUD | 5760 | 9702 | 11715 | 79% | 11682 | 507.7772 | 1018.7213 |  | 2694.8579 | 4758.2775
MYCOM-400LLUD 13768,1070422535 m3/h |  | MYCOM | 400LLUD | 5760 | 11434.5296 | 13807 | 79% | 13768.107 | 598.4533 | 1200.6389 |  | 3176.0907 | 5607.9844
Howden-WRV 163/1.45 662,244897959184 m3/h |  | Howden | WRV 163/1.45 | 390.8837 | 550 | 664.1156 | 79% | 662.2449 | 28.7856 | 57.7506 |  | 152.7697 | 269.7436
Howden-WRV 163/1.80 818,775510204082 m3/h |  | Howden | WRV 163/1.80 | 483.2743 | 680 | 821.0884 | 79% | 818.7755 | 35.5894 | 71.4008 |  | 188.8789 | 333.5012
Howden-WRV 204/1.10 981,326530612245 m3/h |  | Howden | WRV 204/1.10 | 579.2185 | 815 | 984.0986 | 79% | 981.3265 | 42.655 | 85.5759 |  | 226.3769 | 399.711
Howden-WRV 204/1.45 1318,4693877551 m3/h |  | Howden | WRV 204/1.45 | 778.2138 | 1095 | 1322.1939 | 79% | 1318.4694 | 57.3094 | 114.9763 |  | 304.1506 | 537.035
Howden-WRV 204/1.65 1468,97959183673 m3/h |  | Howden | WRV 204/1.65 | 867.051 | 1220 | 1473.1293 | 79% | 1468.9796 | 63.8516 | 128.1014 |  | 338.871 | 598.3404
Howden-WRV 204/1.93 1613,4693877551 m3/h |  | Howden | WRV 204/1.93 | 952.3347 | 1340 | 1618.0272 | 79% | 1613.4694 | 70.1321 | 140.7016 |  | 372.2026 | 657.1936
Howden-WRVi 255/1.10 1914,48979591837 m3/h |  | Howden | WRVi 255/1.10 | 1130.0091 | 1590 | 1919.898 | 79% | 1914.4898 | 83.2164 | 166.9518 |  | 441.6434 | 779.8043
Howden-WRVi 255/1.30 2113,16326530612 m3/h |  | Howden | WRVi 255/1.30 | 1247.2742 | 1755 | 2119.1327 | 79% | 2113.1633 | 91.8521 | 184.277 |  | 487.4743 | 860.7274
Howden-WRVi 255/1.45 2588,77551020408 m3/h |  | Howden | WRVi 255/1.45 | 1527.9998 | 2150 | 2596.0884 | 79% | 2588.7755 | 112.5254 | 225.7525 |  | 597.1907 | 1054.4523
Howden-WRVi 255/1.65 2883,77551020408 m3/h |  | Howden | WRVi 255/1.65 | 1702.1207 | 2395 | 2891.9218 | 79% | 2883.7755 | 125.348 | 251.4778 |  | 665.2427 | 1174.6109
Howden-WRVi 255/1.93 3166,73469387755 m3/h |  | Howden | WRVi 255/1.93 | 1869.1346 | 2630 | 3175.6803 | 79% | 3166.7347 | 137.6473 | 276.1531 |  | 730.517 | 1289.865
Howden-WRV 255/2.20 3841,02040816327 m3/h |  | Howden | WRV 255/2.20 | 2267.1253 | 3190 | 3851.8707 | 79% | 3841.0204 | 166.9562 | 334.9537 |  | 886.0644 | 1564.513
Howden-WRVi 321/1.32 4611,63265306122 m3/h |  | Howden | WRVi 321/1.32 | 2721.9717 | 3830 | 4624.6599 | 79% | 4611.6327 | 200.4522 | 402.1544 |  | 1063.8328 | 1878.3965 |  | 9556.1557 | 9396.8869 | 18953.0426
Howden-WRVi 321/1.65 5767,55102040816 m3/h |  | Howden | WRVi 321/1.65 | 3404.2414 | 4790 | 5783.8435 | 79% | 5767.551 | 250.696 | 502.9556 |  | 1330.4854 | 2349.2217 |  | 4763.2246 | 5321.9415
Howden-WRVi 321/1.93 6333,4693877551 m3/h |  | Howden | WRVi 321/1.93 | 3738.2692 | 5260 | 6351.3605 | 79% | 6333.4694 | 275.2946 | 552.3061 |  | 1461.0341 | 2579.7299
Howden-WRV 321/2.20 7688,0612244898 m3/h |  | Howden | WRV 321/2.20 | 4537.804 | 6385 | 7709.7789 | 79% | 7688.0612 | 334.1741 | 670.4324 |  | 1773.5176 | 3131.4782
Howden-WRVi 365/165 8152,83673469388 m3/h |  | Howden | WRVi 365/165 | 4812.1333 | 6771 | 8175.8673 | 79% | 8152.8367 | 354.3764 | 710.9629 |  | 1880.7341 | 3320.7892
Howden-WRVi 365/193 9536,32653061224 m3/h |  | Howden | WRVi 365/193 | 5628.7248 | 7920 | 9563.2653 | 79% | 9536.3265 | 414.512 | 831.6092 |  | 2199.884 | 3884.3082
Howden-WRV 510/1.32** 9223,26530612245 m3/h |  | Howden | WRV 510/1.32** | 5443.9434 | 7660 | 9249.3197 | 79% | 9223.2653 | 400.9043 | 804.3089 |  | 2127.6656 | 3756.793 | *Swept volume at 3000 rpm except WRV510 range which is measured at 1500rpm **Swept volume at 3600 rpm except WRV510 which is measured at 1800 rpm.
Howden-WRV 510/1.65** 11529,0816326531 m3/h |  | Howden | WRV 510/1.65** | 6804.9293 | 9575 | 11561.6497 | 79% | 11529.0816 | 501.1304 | 1005.3861 |  | 2659.582 | 4695.9912 | *Swept volume at 3000 rpm except WRV510 range which is measured at 1500rpm **Swept volume at 3600 rpm except WRV510 which is measured at 1800 rpm.
Howden-WRV 510/1.93** 12654,8979591837 m3/h |  | Howden | WRV 510/1.93** | 7469.4315 | 10510 | 12690.6463 | 79% | 12654.898 | 550.0658 | 1103.5622 |  | 2919.2905 | 5154.5554 | *Swept volume at 3000 rpm except WRV510 range which is measured at 1500rpm **Swept volume at 3600 rpm except WRV510 which is measured at 1800 rpm.
Howden-XRV 127-R1 352,795918367347 m3/h |  | Howden | XRV 127-R1 | 208.2344 | 293 | 353.7925 | 79% | 352.7959 | 15.3349 | 30.7653 |  | 81.3846 | 143.6998
Howden-XRV 127-R3 478,020408163265 m3/h |  | Howden | XRV 127-R3 | 282.1469 | 397 | 479.3707 | 79% | 478.0204 | 20.7779 | 41.6855 |  | 110.272 | 194.7059
Howden-XRV 127-R4 588,795918367347 m3/h |  | Howden | XRV 127-R4 | 347.5311 | 489 | 590.4592 | 79% | 588.7959 | 25.593 | 51.3456 |  | 135.8262 | 239.8266
Howden-XRV 127-R5 693,551020408163 m3/h |  | Howden | XRV 127-R5 | 409.3618 | 576 | 695.5102 | 79% | 693.551 | 30.1463 | 60.4807 |  | 159.9916 | 282.4951
Howden-XRV 163/1.65 714,020408163265 m3/h |  | Howden | XRV 163/1.65 | 421.4437 | 593 | 716.0374 | 79% | 714.0204 | 31.0361 | 62.2657 |  | 164.7135 | 290.8327
Howden-XRV 163/1.93 854,897959183673 m3/h |  | Howden | XRV 163/1.93 | 504.5953 | 710 | 857.3129 | 79% | 854.898 | 37.1595 | 74.5508 |  | 197.2118 | 348.2145
Howden-XRV 204/1.10 977,714285714286 m3/h |  | Howden | XRV 204/1.10 | 577.0864 | 812 | 980.4762 | 79% | 977.7143 | 42.4979 | 85.2609 |  | 225.5437 | 398.2397
Howden-XRV 204/1.45 1288,36734693878 m3/h |  | Howden | XRV 204/1.45 | 760.4464 | 1070 | 1292.0068 | 79% | 1288.3673 | 56.001 | 112.3512 |  | 297.2065 | 524.774
Howden-XRV 204/1.65 1467,77551020408 m3/h |  | Howden | XRV 204/1.65 | 866.3403 | 1219 | 1471.9218 | 79% | 1467.7755 | 63.7993 | 127.9964 |  | 338.5933 | 597.85
Howden-XRV 204/1.93 1623,10204081633 m3/h |  | Howden | XRV 204/1.93 | 958.0203 | 1348 | 1627.6871 | 79% | 1623.102 | 70.5508 | 141.5416 |  | 374.4247 | 661.1171
| 2940 | GEA GRASSO | LT-P | 572.1115 | 805 | 972.0238 | 79% | 969.2857 | 42.1316 | 84.5259 |  | 223.5993 | 394.8066 | API 619 standard and ISO 10440, respectively
|  | GEA GRASSO | LT-R | 739.1255 | 1040 | 1255.7823 | 79% | 1252.2449 | 54.4309 | 109.2012 |  | 288.8737 | 510.0607 | API 619 standard and ISO 10440, respectively
|  | GEA GRASSO | LT-S | 916.7999 | 1290 | 1557.6531 | 79% | 1553.2653 | 67.5152 | 135.4515 |  | 358.3144 | 632.6714 | API 619 standard and ISO 10440, respectively
|  | GEA GRASSO | LT-T | 1037.6185 | 1460 | 1762.9252 | 79% | 1757.9592 | 76.4126 | 153.3017 |  | 405.5342 | 716.0467 | API 619 standard and ISO 10440, respectively
|  | GEA GRASSO | LT-V | 1236.6138 | 1740 | 2101.0204 | 79% | 2095.102 | 91.067 | 182.702 |  | 483.3078 | 853.3707 | API 619 standard and ISO 10440, respectively
|  | GEA GRASSO | LT-W | 1414.2882 | 1990 | 2402.8912 | 79% | 2396.1224 | 104.1514 | 208.9523 |  | 552.7486 | 975.9815 | API 619 standard and ISO 10440, respectively
|  | GEA GRASSO | LT-Y | 1698.5672 | 2390 | 2885.8844 | 79% | 2877.7551 | 125.0863 | 250.9528 |  | 663.8539 | 1172.1586 | API 619 standard and ISO 10440, respectively
|  | GEA GRASSO | LT-Z | 1952.9969 | 2748 | 3318.1633 | 79% | 3308.8163 | 143.8231 | 288.5432 |  | 763.2931 | 1347.7372 | API 619 standard and ISO 10440, respectively
|  | GEA GRASSO | LT-XA | 2309.7671 | 3250 | 3924.3197 | 79% | 3913.2653 | 170.0965 | 341.2538 |  | 902.7302 | 1593.9396 | API 619 standard and ISO 10440, respectively
|  | GEA GRASSO | LT-XB | 2949.3949 | 4150 | 5011.0544 | 79% | 4996.9388 | 217.2001 | 435.7548 |  | 1152.717 | 2035.3382 | API 619 standard and ISO 10440, respectively
|  | GEA GRASSO | LT-XC | 3482.4181 | 4900 | 5916.6667 | 79% | 5900 | 256.4531 | 514.5057 |  | 1361.0393 | 2403.1705 | API 619 standard and ISO 10440, respectively
|  | GEA GRASSO | LT-XD | 4122.0459 | 5800 | 7003.4014 | 79% | 6983.6735 | 303.5568 | 609.0067 |  | 1611.0261 | 2844.5691 | API 619 standard and ISO 10440, respectively
|  | GEA GRASSO | LT-XE | 5053.0597 | 7110 | 8585.2041 | 79% | 8561.0204 | 372.1187 | 746.5583 |  | 1974.8958 | 3487.0494 | API 619 standard and ISO 10440, respectively
|  | GEA GRASSO | LT-XF | 6083.5712 | 8560 | 10336.0544 | 79% | 10306.9388 | 448.0079 | 898.8099 |  | 2377.6524 | 4198.1916 | API 619 standard and ISO 10440, respectively
| 2950 | Frick | SGC1913 | 592.7218 | 834 | 1007.0408 | 79% | 1004.2041 | 43.6494 | 87.571 |  | 231.6544 | 409.0294
|  | Frick | SGC.1918 | 790.2957 | 1112 | 1342.7211 | 79% | 1338.9388 | 58.1992 | 116.7613 |  | 308.8726 | 545.3726
|  | Frick | SGC.2313 | 1043.304 | 1468 | 1772.585 | 79% | 1767.5918 | 76.8313 | 154.1417 |  | 407.7563 | 719.9702
|  | Frick | SGC.2317 | 1313.3691 | 1848 | 2231.4286 | 79% | 2225.1429 | 96.7195 | 194.0421 |  | 513.3063 | 906.3386
|  | Frick | SGC.2321 | 1622.5226 | 2283 | 2756.6837 | 79% | 2748.9184 | 119.4862 | 239.7177 |  | 634.1332 | 1119.6813
|  | Frick | SGC.2813 | 1869.1346 | 2630 | 3175.6803 | 79% | 3166.7347 | 137.6473 | 276.1531 |  | 730.517 | 1289.865
|  | Frick | SGC.2817 | 2353.8304 | 3312 | 3999.1837 | 79% | 3987.9184 | 173.3414 | 347.7638 |  | 919.9515 | 1624.347
|  | Frick | SGC.2821 | 2832.1298 | 3985 | 4811.8197 | 79% | 4798.2653 | 208.5644 | 418.4296 |  | 1106.8861 | 1954.4152
|  | Frick | SGC.2824 | 3198.8498 | 4501 | 5434.881 | 79% | 5419.5714 | 235.5705 | 472.6102 |  | 1250.2118 | 2207.4837
|  | Frick | SGCH/B.3511 | 2928.074 | 4120 | 4974.8299 | 79% | 4960.8163 | 215.63 | 432.6048 |  | 1144.3841 | 2020.625
|  | Frick | SGCH/B.3515 | 3992.699 | 5618 | 6783.6395 | 79% | 6764.5306 | 294.0314 | 589.8965 |  | 1560.4733 | 2755.3085
|  | Frick | SGCH/B.3519 | 5081.4876 | 7150 | 8633.5034 | 79% | 8609.1837 | 374.2122 | 750.7583 |  | 1986.0064 | 3506.6671
|  | Frick | SGCB.3524 | 6419.7312 | 9033 | 10907.1939 | 79% | 10876.4694 | 472.7635 | 948.4755 |  | 2509.0343 | 4430.1712
|  | Aerzen | VMY236H (DP<20 b) | 496.7776 | 699 | 844.0306 | 79% | 841.6531 | 36.5838 | 73.3958 |  | 194.1564 | 342.8196 | Attention , Delta P max spécifié !
|  | Aerzen | VMY236M (DP<16 b) | 653.8418 | 920 | 1110.8844 | 79% | 1107.7551 | 48.1504 | 96.6011 |  | 255.5421 | 451.2075 | Attention , Delta P max spécifié !
|  | Aerzen | VMY236B (DP<8 b) | 867.7617 | 1221 | 1474.3367 | 79% | 1470.1837 | 63.9039 | 128.2064 |  | 339.1488 | 598.8308 | Attention , Delta P max spécifié !
|  | Aerzen | VMY336H (DP<20 b) | 981.4733 | 1381 | 1667.534 | 79% | 1662.8367 | 72.2779 | 145.0066 |  | 383.5909 | 677.3017 | Attention , Delta P max spécifié !
|  | Aerzen | VMY336M (DP<16 b) | 1285.6519 | 1809 | 2184.3367 | 79% | 2178.1837 | 94.6783 | 189.9471 |  | 502.4735 | 887.2113 | Attention , Delta P max spécifié !
|  | Aerzen | VMY336B (DP<8 b) | 1713.4918 | 2411 | 2911.2415 | 79% | 2903.0408 | 126.1854 | 253.1578 |  | 669.6869 | 1182.458 | Attention , Delta P max spécifié !
|  | Aerzen | VMY436H (DP<20 b) | 1924.569 | 2708 | 3269.8639 | 79% | 3260.6531 | 141.7296 | 284.3431 |  | 752.1826 | 1328.1195 | Attention , Delta P max spécifié !
|  | Aerzen | VMY436M (DP<16 b) | 2528.662 | 3558 | 4296.2245 | 79% | 4284.1224 | 186.2164 | 373.5941 |  | 988.2812 | 1744.996 | Attention , Delta P max spécifié !
|  | Aerzen | VMY436B (DP<8 b) | 3363.7316 | 4733 | 5715.017 | 79% | 5698.9184 | 247.7128 | 496.9705 |  | 1314.6529 | 2321.2665 | Attention , Delta P max spécifié !
|  | Aerzen | VMY536H (DP<20 b) | 4050.2655 | 5699 | 6881.4456 | 79% | 6862.0612 | 298.2707 | 598.4016 |  | 1582.9721 | 2795.0344 | Attention , Delta P max spécifié !
|  | Aerzen | VMY536M (DP<16 b) | 5301.0932 | 7459 | 9006.6156 | 79% | 8981.2449 | 390.3845 | 783.2037 |  | 2071.8352 | 3658.214 | Attention , Delta P max spécifié !
|  | Aerzen | VMY536B (DP<8 b) | 7062.2018 | 9937 | 11998.7585 | 79% | 11964.9592 | 520.0765 | 1043.3965 |  | 2760.1322 | 4873.5316 | Attention , Delta P max spécifié !

## Howden
HOWDEN COMPRESSOR SPECIFICATION | *SWEPT VOLUME 50Hz | *SWEPT VOLUME 60Hz | SUCTION PORT Ø | DISCHARGE PORT Ø | A | B | C | D | WEIGHT APPROX.
| m3/hr | m3/hr | mm | mm | mm | mm | mm | mm | kg | 1.6923
WRV 163/1.45 | 550 | 660 | 125 | 75 | 1063 | 490 | 248 | 250 | 470
WRV 163/1.80 | 680 | 820 | 125 | 75 | 1120 | 490 | 248 | 250 | 495
WRV 204/1.10 | 815 | 975 | 150 | 100 | 1201 | 640 | 310 | 315 | 760
WRV 204/1.45 | 1095 | 1315 | 200 | 125 | 1273 | 640 | 310 | 315 | 850
WRV 204/1.65 | 1220 | 1464 | 200 | 125 | 1314 | 640 | 310 | 315 | 887
WRV 204/1.93 | 1340 | 1608 | 200 | 125 | 1370 | 640 | 310 | 315 | 925
WRVi 255/1.10 | 1590 | 1908 | 200 | 150 | 1493 | 692 | 349 | 362 | 1200
WRVi 255/1.30 | 1755 | 2106 | 200 | 150 | 1544 | 692 | 349 | 362 | 1270
WRVi 255/1.45 | 2150 | 2580 | 255 | 200 | 1583 | 692 | 349 | 362 | 1325
WRVi 255/1.65 | 2395 | 2874 | 255 | 200 | 1633 | 692 | 349 | 362 | 1422
WRVi 255/1.93 | 2630 | 3156 | 255 | 200 | 1705 | 692 | 349 | 362 | 1540
WRV 255/2.20 | 3190 | 3828 | 255 | 200 | 1815 | 692 | 349 | 362 | 1650
WRVi 321/1.32 | 3830 | 4596 | 255 | 200 | 2005 | 940 | 471 | 500 | 2925
WRVi 321/1.65 | 4790 | 5748 | 300 | 255 | 2110 | 940 | 471 | 500 | 3150
WRVi 321/1.93 | 5260 | 6312 | 300 | 255 | 2200 | 940 | 471 | 500 | 3260
WRV 321/2.20 | 6385 | 7662 | 350 | 300 | 2345 | 940 | 471 | 500 | 3500
WRVi 365/165 | 6771 | 8125.2 | 350 | 300 | 2418 | 1125 | 565 | 590 | 5500
WRVi 365/193 | 7920 | 9504 | 350 | 300 | 2520 | 1125 | 565 | 590 | 6100
WRV 510/1.32 | 7660 | 9192 | 350 | 255 | 2920 | 1560 | 750 | 750 | 10800
WRV 510/1.65 | 9575 | 11490 | 400 | 300 | 3090 | 1560 | 750 | 750 | 11500
WRV 510/1.93 | 10510 | 12612 | 400 | 300 | 3233 | 1560 | 750 | 750 | 11800
XRV 127
XRV 127-R1 | 293 | 352 | 100 | 50 | 850 | 390 | 299 | 201 | 250
XRV 127-R3 | 397 | 476 | 100 | 50 | 900 | 390 | 209 | 291 | 250
XRV 127-R4 | 489 | 586 | 100 | 50 | 900 | 390 | 209 | 291 | 250
XRV 127-R5 | 576 | - | 100 | 50 | 900 | 390 | 209 | 291 | 250
XRV 163 & XRV 204 Compressors
XRV 163/1.65 | 593 | 712 | 125 | 76 | 1070 | 430 | 200 | 250 | 364
XRV 163/1.93 | 710 | 852 | 125 | 76 | 1116 | 430 | 200 | 250 | 388
XRV 204/1.10 | 812 | 974 | 150 | 100 | 1178 | 516 | 240 | 305 | 636
XRV 204/1.45 | 1070 | 1284 | 150 | 100 | 1249 | 516 | 240 | 305 | 660
XRV 204/1.65 | 1219 | 1463 | 150 | 100 | 1255 | 516 | 240 | 305 | 690
XRV 204/1.93 | 1348 | 1618 | 150 | 100 | 1312 | 516 | 240 | 305 | 736
The company operates a policy of continuous product development and reserves the right to alter the data provided without notice.
*Swept volume at 3000 rpm except WRV510 range which is measured at 1500rpm **Swept volume at 3600 rpm except WRV510 which is measured at 1800 rpm.
L/D : Lentgh over diameter is around 1,4 to 2,1

## MYCOM
L | 2.63
M | 3.65
H | 5.8

## Frick
GEOMETRICAL SWEPT VOLUME
| Compressor Model | Rotor Diameter mm | Rotor L/D | Max Speed RPM | Geometrical Swept Volume Drive Shaft End |  | CFM 3550 RPM | m³/h 2950 RPM | Rotor
[5 empty] | ft³/ Rev | m³/Rev |  |  | L
| SGC1913 | 193 | 1.35 | .4,500. | 0.16653 | 0.004713 | 591 | 834 | 260.55
HOUSING: Cast Iron | SGC.1918 | 193 | 1.8 | .4,500. | 0.22204 | 0.006284 | 788 | 1112 | 347.4
ROTORS: Asymmetric 4+6 | SGC.2313 | 233 | 1.35 | .4,500. | 0.29301 | 0.008292 | 1040 | 1468 | 314.55
BEARINGS: Antifriction | SGC.2317 | 233 | 1.7 | .4,500. | 0.36897 | 0.010442 | 1310 | 1848 | 396.1
SHAFT SEAL: Stationary carbon | SGC.2321 | 233 | 2.1 | .4,500. | 0.4558 | 0.012899 | 1618 | 2283 | 489.3
VOLUME RATIO CONTROL: Variable 2.2 – 5.0 | SGC.2813 | 283 | 1.35 | .4,200. | 0.52501 | 0.014858 | 1864 | 2630 | 382.05
CAPACITY CONTROL: Variable 12% - 100% | SGC.2817 | 283 | 1.7 | .4,200. | 0.66115 | 0.018711 | 2347 | 3312 | 481.1
LUBRICATION SYSTEM: No Oil Pump | SGC.2821 | 283 | 2.1 | .4,200. | 0.79546 | 0.022512 | 2824 | 3985 | 594.3
OIL SEPARATOR/RESERVOIR: ASME 300 psi DWP | SGC.2824 | 283 | 2.4 | .4,200. | 0.89858 | 0.02543 | 3190 | 4501 | 679.2
OIL FILTERS: 5 Micron Absolute | SGCH/B.3511 | 355 | 1.1 | .4,200. | 0.82248 | 0.023276 | 2920 | 4120 | 390.5
| SGCH/B.3515 | 355 | 1.5 | .4,200. | 1.1215 | 0.031739 | 3981 | 5618 | 532.5
| SGCH/B.3519 | 355 | 1.9 | .4,200. | 1.4275 | 0.040398 | 5068 | 7150 | 674.5
| SGCB.3524 | 355 | 2.4 | .4,200. | 1.8033 | 0.051033 | 6402 | 9033 | 852

## Aerzen
15
VMY236H (DP<20 b) | 699
VMY236M (DP<16 b) | 920
VMY236B (DP<8 b) | 1221
VMY336H (DP<20 b) | 1381
VMY336M (DP<16 b) | 1809
VMY336B (DP<8 b) | 2411
VMY436H (DP<20 b) | 2708
VMY436M (DP<16 b) | 3558
VMY436B (DP<8 b) | 4733
VMY536H (DP<20 b) | 5699
VMY536M (DP<16 b) | 7459
VMY536B (DP<8 b) | 9937

## Sheet2
air molar mass | 28.9586
[27 empty] | L | 2.63
[27 empty] | M | 3.65
[27 empty] | H | 5.8
air density | 1.2758 | [15 empty] | Actual flow (process need) | [5 empty] | NEED (screw displacement)
|  |  |  | Power @4,5K | Tmoy | Rdt W/W | Rdt % | Rdt expected (Green) | Power WCS (kW) | T (K) | LP (bar abs) | MP (bar abs) | HP (bar abs) | m_LP | m_HP | LP/HP | LP (Am3/h) | HP (Am3/h) | %vol LP | %vol HP | Nb_LP | Nb_HP | LP (Am3/h) | HP (Am3/h) | Screw LP | Screw HP | RPM | RPM | LP Am3/h | HP Am3/h | HX1 UA
|  | KSTAR | 4,5K | 9.6 | 28 | 268 | 24.5% | 26.08% | 2573.0612 | 312 | 1.03 | 5.2 | 22 | 496.3 | 996.3 | 2.5149 | 11243.2639 | 4470.6651 | 80% | 75% | 2 | 2 | 7027.0399 | 2980.4434 | 400SUD-MB | 320SUD-L |  |  |  |  | 369272
|  | Qatar 1 | [7 empty] | 318 | 1.071 | 3.957 | 20.62 | 463.1 | 1547 | 1.106 | 10283.553 | 9297.8416 | 80% | 75% | 2 | 2 | 6427.2206 | 6198.5611 | 400MUD-LB | 400SUD-L | 2985 | 2975 | 8027 | 6463
|  | Qatar 2 | [7 empty] | 320.5 | 1.05 | 4.825 | 21 | 886.5 | 4067 | 1.0016 | 20237.0979 | 20203.9203 | 80% | 75% | 2 | 2 | 12648.1862 | 13469.2802
|  | Qatar 3 | [7 empty] | 320 | 1.05 | 4.825 | 21 | 254.3 | 1243 | 0.94012 | 5796.1257 | 6165.3047 | 80% | 75% | 2 | 2 | 3622.5786 | 4110.2032
|  | ESS | [7 empty] | 311 | 1.05 | 4 | 16 | 424.2 | 1034 | 1.5629 | 9396.6384 | 6012.453 | 80% | 75% | 2 | 2 | 5872.899 | 4008.302
|  | TMCP | 20K | [6 empty] | 297 | 3.4 | 20 |  | 1196 |  |  | 7813.3894 | 0 | 80% | 75% | 2 | 2 | 4883.3684 | 0
|  | LEP 12kW | [7 empty] | 307.8 | 1.04 | 4.3 | 17.6 | 570.7 | 977.7 | 2.4134 | 12632.0521 | 5234.0339 | 80% | 75% | 2 | 2 | 7895.0326 | 3489.356
SNS20K