## Aerzen
Vi = Vs/Vd
air molar mass | 28.9586 | Pi = Vi^k
|  | L | 2.63 |  |  | 2.63
air density | 1.2758 | M | 3.65 |  |  | 3.65
|  | H | 5.8 |  |  | 5.8
|  | Pi = Vi^k | 8.5784 |  |  | 8.5784
4.0026
28.0135
16.0428
39.948 |  |  | HE400LLUD-LB |  |  | ammoniac
2.0159
28.9586 |  | Fluid | helium |  |  | ammonia
28.0101 |  | Components | Mole Fractions |  |  | Mole Fractions
31.9988 |  | helium | 100% |  |  | 100%
|  | nitrogen | 0% |  |  | 0%
|  | methane | 0% |  |  | 0%
|  | argon | 0% |  |  | 0%
|  | hydrogen | 0% |  |  | 0%
|  | air | 0% |  |  | 0%
|  | carbon monoxide | 0% |  |  | 0%
|  | oxygen | 0% |  |  | 0%
|  | Total | 1 |  |  | 1
|  | Srew displacement | 5699 |  |  | 6540
|  | Volumetric Efficiency | 90.35% |  |  | 82.2%
|  | Volumetric flow | 5148.8401 |  |  | 5376.08
|  | Flow Nm3/h | 21760.88 |  |  | 4925.2935
|  | Flow kg/h | 3826.8 |  |  | 3732.1589
|  | Flow g/s | 1063 |  |  | 1036.7108
|  | Mol Wgt | 4.0026 |  |  | 17.0303
|  | Gamma | 1.6697 |  |  | 1.302
|  | Cp | 5.1932 |  |  | 2.1635
|  | Pout / Pin | 4 |  |  | 5
|  | T In | 50 |  |  | 25
|  | P In | 5 |  |  | 1
|  | P In | 5 |  |  | 1
|  | P Out | 20 |  |  | 5
3.8 |  | CR : Compression Ratio | 4 |  |  | 5
2.2245 |  | Ideal Vi | 2.2939 |  |  | 3.4423
|  | Choosen Vi = Vs/Vd | 3 |  |  | 2.63
|  | Internal pressure ratio Pi = Vi ^ gamma | 6.2612 |  |  | 3.5219
|  | Internal pressure / external pressure | 156.5% |  |  | 70.44%
|  | Isothermal Power m.R.T.ln(P2/P1) | 989.1462 |  |  | 242.8597
|  | Isothermal Power P.Qv.ln(P2/P1) | 991.3622 |  |  | 240.3463
|  | Adiabatique Power m.R.T.gamma/(gamma-1)*((P2/P1)^.. | 1323.0689 |  |  | 294.3969
38.3 |  | Motor efficiency | 95% |  |  | 95%
35.86 |  | Itensity | 172.0708 |  |  | 51.8796
2.44
|  | Overall Power | 1790.0002 |  |  | 539.6882
|  | Isothermal Efficiency | 55.26% |  |  | 45%
|  | Adiabatique Efficiency | 73.91% |  |  | 54.55%
|  | Tout before after cooler (Tin Oil cooler) | 80 |  |  | 80
|  | T out | 36.1026 |  |  | 36.1026
|  | dT Tout / Water in | 6.1026 |  |  | 6.1026
|  | dT Tout oil / Water in | 3 |  |  | 3
|  | dT water inlet/outlet | 10 |  |  | 10
HELIUM AFTER COOLER
|  | Water inlet | 30 |  |  | 30
|  | Water outlet | 31.7345 |  |  | 32.3056
|  | dT water | 1.7345 |  |  | 2.3056
|  | Water Flow | 120.3278 |  |  | 36.7794
|  | He inlet after cooler | 80 |  |  | 80
|  | He outlet after cooler | 36.1026 |  |  | 36.1026
|  | DTML | 20.3882 |  |  | 20.2285
|  | Power helium to be extracted by after cooler | 242.3308 |  |  | 98.459
|  | UA | 11.8858 |  |  | 4.8673
|  | Margins on surface | 0% |  |  | 0%
|  | P=UA x DTML x margins | 242.3308 |  |  | 98.459
Convergence
OIL COOLER
|  | Water inlet | 31.7345 |  |  | 32.3056
|  | Water outlet | 40 |  |  | 40
|  | Water Flow | 163.6897 |  |  | 36.7794
|  | Oil inlet | 80 |  |  | 80
|  | Oil outlet going through cooler | 34.7345 |  |  | 35.3056
|  | Oil injected in screw (mix by-pass & cooled) | 34.7345 |  |  | 35.3056
|  | cp oil | 1.95 |  |  | 1.95
|  | Density (kg/m3) | 980 |  |  | 980
|  | T Out Adiab | 290.3415 |  |  | 159.9152
|  | DT extracted by oil cooler | 210.3415 |  |  | 79.9152
|  | Power to be extracted by oil | 1570.9607 |  |  | 328.5912
|  | Oil mass Flow | 64071.6168 |  |  | 13572.8263
|  | Oil Flow | 65.3792 |  |  | 13.8498
|  | % oil flow by-passing cooler | 0% |  |  | 0%
|  | Oil Flow | 1089.6533 |  | 0 | 230.8304
|  | F : Factor for DTM calc. | 0.92256 |  |  | 0.92256
|  | DTM = F x DTML | 13.178 |  |  | 13.178
|  | UA = UAref x (m/mref) | 119.2109 |  | 0 | 24.9348
|  | Margins on surface | 0% |  |  | 0%
|  | P=UA x DTML | 1570.9607 |  |  | 328.5912
Convergence
|  | converge water flow as in serial | -43.3618 |  |  | 1.6338e-06
|  | Total Flow gas | 1223.0799 |  |  | 1058.4332
|  | Ratio oil/gas | 5.345% |  |  | 1.309%
|  | rho_inlet | 0.74324 |  |  | 0.69422
|  | rho_outlet | 3.1288 |  |  | 3.5261
|  | rho_Nm3 | 0.17615 |  |  | 0.17615
|  | Water TOTAL Delta T | 10 |  |  | 10
|  | Needed Overall Water Flow (Mech Power/DT) | 154.1627 |  | #DIV/0! | 46.4803
|  | Power coolers | 1813.2915 |  |  | 427.0502
|  | Power to be extracted | 1790.0002 |  |  | 539.6882
|  |  | 23.2913 |  |  | -112.638
P
R
|  | Kynematic Viscosity (cSt =10-6 m2/s = 1 mm2/s | 11.2881 |  |  | 11.2881
|  | Absolute Viscosity (Pa.s = 1 N s/m2 = 1 kg/m.s) | 0.011062 |  |  | 0.011062
|  |  | 0 |  |  | 0
|  |  | 0.27735 |  |  | 0.058012
|  | lambda | 0.1451 |  |  | 0.1451
|  |  | 0.6291 |  |  | 0.6291
|  |  | 0.11791 |  |  | 0.11791
|  | P | 2895060 | W |  | 2895060
|  | DTML | 20.43 |  |  | 20.43
|  | A | 429.82 | m² |  | 429.82
|  | U | 329.6876 | W/m².K |  | 329.6876
|  |  | 1.1344 |  |  | 1.1344

## Sheet1
|  |  | DESIGN | Maxi |  | Maxi | Maxi |  |  |  | Maxi | DESIGN | DESIGN |  | Maxi | Maxi | OFFER - MAXI 11/07/2003 | OFFER - MAXI 11/07/2003 | DESIGN
| air molar mass | 28.9586 | 4032SS | 4032SS |  | 4032SS | 4032SS |  |  |  | 4032SS | 4032SS | 4032SS |  | 4032SS | 4032SS | 4032SS | 4032SS | 4032SS
| air density | 1.2758 | helium;0,49589;nitrogen;0,47595;methane;0,01935;argon;0,00029;hydrogen;0,00826;carbon monoxide;0,00003;oxygen;2,29999999999952E-04 | helium;0,52133;nitrogen;0,45101;methane;0,01785;argon;0,000035;hydrogen;0,00759;carbon monoxide;0,00003;oxygen;2,29999999999952E-04 |  | air | air |  |  |  | helium;0,52133;nitrogen;0,45101;methane;0,01785;argon;0,000035;hydrogen;0,00759;carbon monoxide;0,00003;oxygen;2,29999999999952E-04 | helium;0,49589;nitrogen;0,47595;methane;0,01935;argon;0,00029;hydrogen;0,00826;carbon monoxide;0,00003;oxygen;2,29999999999952E-04 | helium;0,49589;nitrogen;0,47595;methane;0,01935;argon;0,00029;hydrogen;0,00826;carbon monoxide;0,00003;oxygen;2,29999999999952E-04 |  | helium | helium | helium;0,49589;nitrogen;0,47595;methane;0,01935;argon;0,00029;hydrogen;0,00826;carbon monoxide;0,00003;oxygen;2,29999999999952E-04 | helium;0,49589;nitrogen;0,47595;methane;0,01935;argon;0,00029;hydrogen;0,00826;carbon monoxide;0,00003;oxygen;2,29999999999952E-04 | helium;0,49589;nitrogen;0,47595;methane;0,01935;argon;0,00029;hydrogen;0,00826;carbon monoxide;0,00003;oxygen;2,29999999999952E-04
|  | Components | Mole Fractions | Mole Fractions |  | Mole Fractions | Mole Fractions |  |  |  | Mole Fractions | Mole Fractions | Mole Fractions |  | Mole Fractions | Mole Fractions | Mole Fractions | Mole Fractions | Mole Fractions
| 4.0026 | helium | 49.59% | 52.13% | [6 empty] | 52.13% | 49.59% | 49.59% |  |  |  | 49.59% | 49.59% | 49.59%
| 28.0135 | nitrogen | 47.59% | 45.1% | [6 empty] | 45.1% | 47.59% | 47.6% |  |  |  | 47.59% | 47.6% | 47.59%
| 16.0428 | methane | 1.935% | 1.785% | [6 empty] | 1.785% | 1.935% | 1.935% |  |  |  | 1.935% | 1.935% | 1.935%
| 39.948 | argon | 0.029% | 0.0035% | [6 empty] | 0.0035% | 0.029% | 0.029% |  |  |  | 0.029% | 0.029% | 0.029%
| 2.0159 | hydrogen | 0.826% | 0.759% | [6 empty] | 0.759% | 0.826% | 0.826% |  |  |  | 0.826% | 0.826% | 0.826%
| 28.9586 | air | [16 empty] | 0%
| 28.0101 | carbon monoxide | 0.003% | 0.003% | [6 empty] | 0.003% | 0.003% | 0.003% |  |  |  | 0.003% | 0.003% | 0.003%
| 31.9988 | oxygen | 0.023% | 0.023% | [6 empty] | 0.023% | 0.023% | 0.023% |  |  |  | 0.023% | 0.023% | 0.023%
density normal |  | Total | 1 | 0.99807 |  | 0 | 0 |  |  |  | 0.99807 | 1 | 1 |  | 0 | 0 | 1 | 1 | 1
|  |  |  | 15.0323 | g/mol | 0 | 0 |  | 1051 |  | 0.47557 |  |  |  | 0 | 0
|  |  |  | 0.86577 | kg/m3 | 9912.782 | [5 empty] | 0.68942 | 0.68942 |  | #VALUE! | #VALUE! | 0.68942 | 0.68942 | 0.68942
|  |  | 0.90399 | 0.86632 | kg/m3 | 1.6354 | 3.7775 |  | 1.6607 | 3.8015 | 0.84972 | 0.88378 | 1.9043 |  | 0.1767 | 0.1767 | 0.90399 | 1.9478 | 0.90399
#VALUE! |  |  | 15.7108 | 13.4711 |  | 3.8923 | 27.0236
|  |  | A - S4 | A - S4 |  | A - S4 | A - S4 |  | A - S4 | A - S4 | A - S4 | A - S4 | A - S4 |  | A - S4 | A - S4 | A - S4 | A - S4 | A - S4
#VALUE! | 0.22108 |  | 49 | 49 |  | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49
|  |  | 2940 | 2940 |  | 2940 | 2940 |  | 2940 | 2940 | 2940 | 2953 | 2940 |  | 2940 | 2940 | 2953 | 2940 | 2940
|  | Displacment | 6440 | 6440 | 1 | 6560 | 3210 |  | 6560 | 3210 | 6520 | 6520 | 6520 |  | 6740 | 5600 | 6520 | 3190
|  | Displacment | 3793.16 | 6440 | 1.6978 | [11 empty] | 6520 | 3190
|  | Efficiency | 82.99% | 91.93% | 1.1078 | 92.4% | 82.7% |  | 92.4% | 82.7% | 80.75% | 92.3% | 74.43% |  | 91.1% | 91.1% | 92.3% | 74.43%
|  | Volumetric flow | 5344.3152 | 5920.2331 | 1.1078 | 6061.44 | 2654.67 |  | 6061.44 | 2654.67 | 5265.1372 | 6017.7 | 4852.9044 |  | 6140.14 | 5101.6 | 6017.7 | 2374.3505 | 7000
|  |  | 7009.3273 | 7739.3917 |  | 7772.1636 | 7862.913 |  | 7772.1636 | 7884.8765 | 6751.1198 | 7716.0788 | 13418.6798 |  | 6159.2085 | 5117.4432 | 7892.504 | 6715.3867
|  | Flow | 4831.2 | 5128.792 |  | 9912.782 | 10028.1117 |  | 10066.2952 | 10091.6649 | 0 | 0.17675 | 0.14254 |  | #VALUE! | #VALUE! | 0.17675 | 0.14254 | 0
|  | Flow | 1342 | 1424.6645 |  | 2753.5505 | 2785.5866 |  | 2796.1931 | 2803.2402 | 1242.7442 | 1477.3114 | 2567.0113 |  | 301.3721 | 250.3982 | 1511.0923 | 1284.6671 | 1757.7556
|  | Mol Wgt | 15.6647 | 15.0613 |  | 28.9586 | 28.9586 |  | 28.81 | 28.82 | 15.0613 | 15.6647 | 15.6647 |  | 4.0026 | 4.0026 | 15.6647 | 15.6647 | 15.6647
|  | Gamma | 1.4965 | 1.5033 |  | 1.4015 | 1.4036 |  | 1.4 | 1.4 | 1.5031 | 1.4963 | 1.4983 |  | 1.6674 | 1.6674 | 1.4577 | 1.4585 | 1.4955
|  | Cp | 1.6047 | 1.6538 |  | 1.0078 | 1.0114 |  | 1.4 | 1.4 | 1.6541 | 1.6051 | 1.6062 |  | 5.1932 | 5.1932 | 1.6047 | 1.6058 | 1.6047 | Power = Uicosphi
|  | Pout / Pin | 17.415 | 17.6871 |  | 2.4558 | 7.1508 |  | 2.4558 | 7.1309 | 17.415 | 2.449 | 8.0757 |  | 4.3478 | 4.3478 | 2.449 | 8.0757 | 17.415
| 306.15 | T In | 33 | 34 |  | 40 | 57 |  | 40 | 57 | 40 | 40 | 40 |  | 40 | 40 | 33 | 33 | 33
|  | P In | 1.5 | 1.5 |  | 1.5 | 3.61 |  | 1.5 | 3.62 | 1.5 | 1.5 | 3.2 | , |  |  | 1.5 | 3.2 | 1.5
|  | P In | 1.47 | 1.47 |  | 1.47 | 3.58 |  | 1.47 | 3.59 | 1.47 | 1.47 | 3.17 |  | 1.15 | 1.15 | 1.47 | 3.17 | 1.47
|  | P Out | 25.6 | 26 |  | 3.61 | 25.6 |  | 3.61 | 25.6 | 25.6 | 3.6 | 25.6 |  | 5 | 5 | 3.6 | 25.6 | 25.6
|  | Isothermal Power m.R.T.ln(P2/P1) | 623.0663 | 693.9393 |  | 222.4178 | 519.4162 |  | 227.0273 | 524.477 | 613.8219 | 219.9178 | 891.2033 |  | 288.1009 | 239.3717 | 219.9181 | 436.0351 | 816.0941
|  | Isothermal Power P.Qv.ln(P2/P1) | 623.5443 | 694.4871 |  | 222.3731 | 519.3332 |  | 222.3731 | 520.0454 | 614.3062 | 220.0869 | 892.6228 |  | 288.2672 | 239.5098 | 220.0869 | 436.728
117.6194 |  | Motor efficiency | 95% | 95% |  | 95% | 95% |  | 95% | 95% | 95% | 95% | 95% |  | 95% | 95% | 95% | 95% | 95% |  | 6520
|  | Overall Power | 1258.7198 | 1387.8785 |  | 380 | 927.3 |  | 380 | 927.3 | 1310.0594 | 444.2783 | 1803.2784 |  | 544.6142 | 457.6896 | 444.2791 | 882.2789 | 1648.675 |  | 6017.7
|  | Isothermal Efficiency | 49.5% | 50% |  | 58.53% | 56.01% |  | 59.74% | 56.56% | 46.85% | 49.5% | 49.5% |  | 52.9% | 52.3% | 49.5% | 49.5% | 49.5% |  | 0.92296
|  | Cust max Water Temp | 38 | 30 |  | 50 | 57 |  | 50 | 57 | 50 | 38 | 38 |  | 50 | 50 | 38 | 38 | 38
|  | dT Water/Oil | 3 | 3 |  | 0 | 0 |  | 0 | 0 | 3 | 10 | 10 |  | 0 | 0 | 10 | 10 | 10
|  | dT Water/He | 7 | 3 |  |  | 3 |  |  | 3 | 3 | 7 | 7 |  | 3 | 3 | 7 | 7 | 7
| 342.95 | Tout before after cooler | 69.8 | 72 |  | 57 | 77 |  | 57 | 71.7 | 77 | 69.8 | 69.8 |  | 95.6 | 89.5 | 69.8 | 69.8 | 69.8
| 318.15 | T out | 45 | 33 |  | 57 | 60 |  | 57 | 60 | 53 | 45 | 45 |  | 53 | 53 | 45 | 45 | 45
|  | Water Delta T | 10 | 10 |  | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10
|  | Needed Overall Water Flow (Mech Power/DT) | 108.4065 | 119.5302 |  | 32.7273 | 79.8632 |  | 32.7273 | 79.8632 | 112.8281 | 38.2632 | 155.3063 |  | 46.9046 | 39.4182 | 38.2633 | 75.9857 | 141.9911
|  | Water to cool oil | 103.807 | 111.6166 |  | 32.7273 | 75.7384 |  | 32.7273 | 75.9086 | 108.5791 | 33.1985 | 146.4997 |  | 41.1624 | 35.3305 | 33.0842 | 71.5796 | 135.9667
|  | Water to cool Helium | 4.5995 | 7.9136 |  | 0 | 4.1247 |  | 0 | 3.9546 | 4.249 | 5.0647 | 8.8066 |  | 5.7421 | 4.0878 | 5.1791 | 4.4062 | 6.0245
|  | Tin Oil | 41 | 33 |  | 50 | 57 |  | 50 | 57 | 53 | 48 | 48 |  | 50 | 50 | 48 | 48 | 48
|  | cp oil | 2.19 | 2.19 |  | 1.95 | 1.95 |  | 1.95 | 1.95 | 2.19 | 2.19 | 2.19 |  | 2 | 2 | 2.19 | 2.19 | 2.19
|  | Density (kg/m3) | 980 | 980 |  | 983 | 983 |  | 983 | 983 | 980 | 980 | 980 |  | 879 | 879 | 980 | 980 | 980
|  | Kynematic Viscosity (cSt =10-6 m2/s = 1 mm2/s | 14.4081 | 13.6748 |  | 19.7802 | 12.1012 |  | 19.7802 | 13.7304 | 12.1382 | 14.4081 | 14.4081 |  | 8.544 | 9.9331 | 14.4081 | 14.4081 | 14.4081
|  | Absolute Viscosity (Pa.s = 1 N s/m2 = 1 kg/m.s) | 0.01412 | 0.013401 |  | 0.019444 | 0.011895 |  | 0.019444 | 0.013497 | 0.011895 | 0.01412 | 0.01412 |  | 0.0075102 | 0.0087312 | 0.01412 | 0.01412 | 0.01412
[12 empty] | 10463.9711 | 46175.8539 |  |  |  | 10427.9458 | 22561.4573 | 42855.8997
|  | T Out Adiab | 516.8927 | 530.4634 |  | 131.9245 | 308.1406 |  | 131.6451 | 305.5682 | 541.6927 | 38.4391 | 169.6256 |  | 290.7848 | 290.7848 | 38.3067 | 82.8788 | 157.4298
|  | DT extracted by oil cooler | 447.0927 | 458.4634 |  | 74.9245 | 231.1406 |  | 74.6451 | 233.8682 | 464.6927 |  |  |  | 195.1848 | 201.2848
|  | Power extracted by oil | 962.7939 | 1080.1599 |  | 355.2377 | 1162.5175 |  | 292.2109 | 917.8244 | 955.2495 |  |  |  | 305.4803 | 261.7437
|  | Needed Oil flow | 62.5959 | 50.329 |  | 95.3093 | 109.1651 |  | 78.3994 | 117.2618 | 76.3009 |  |  |  | 13.7184 | 13.5695
169986258 | [5 empty] | 1588.4885 | 1819.4186 |  | 1306.6568 | 1954.3636
|  | Power extracted by oil | -200.0584 | -196.4549 |  | 353.4 | 862.389 |  | 353.4 | 862.389 | -202.9734 | 0 | 0 |  | 462.9221 | -61.2743 | 0 | 0 | 0
|  | Flow | -303.8654 | -308.0715 | [6 empty] | -311.5525 |  |  |  |  | -96.6048
|  | Needed Oil flow | -256.7055 | -272.3352 |  | 94.8163 | 80.9818 |  | 94.8163 | 110.1794 | -319.0298 |  |  |  | 20.7887 | -19.321
|  | Needed Oil flow | #DIV/0! | #DIV/0! |  | 1580.2712 | 1349.6972 |  | 1580.2712 | 1836.3227 | #DIV/0! |  |  |  | 346.4778 | #DIV/0!
[6 empty] | 0.93125 |  |  | 0.93125
[6 empty] | 230.574 |  |  | -256.0515
863115.6572
[6 empty] | 909233.4093 |  |  | -647.7069 | [5 empty] | 228.6392 | 226.1578
|  |  | 1095.6848 |  |  | 46.1178 |  |  | 117.222 |  |  | 148.318 | 354.1239 |  |  |  | 132.4195 | 317.2148 | 515.8234
|  | G=0.03Vth+10 | 210.1779 | [8 empty] | 108.318 | 314.1239 |  |  |  | 99.4195 | 284.2148 | 482.8234
|  | Vi | 6.7485 | [9 empty] | 123.7578 |  | 599.86 |  |  | 76.3772
% Power
|  | Power T | 962.7939 | 1080.1599 |  | 207.9242 | 651.1705 |  | 292.2109 | 917.8244 | 955.2495 | 256.8487 | 1295.1792 |  | 305.4803 | 261.7437 | 241.0714 | 586.3162 | 1361.8524
|  | Power P | 67.1605 | 76.8157 |  | 28.4104 | 89.6766 |  | 28.9992 | 90.5503 | 78.4061 | 28.091 | 113.8372 |  | 36.8004 | 30.576 | 23.705 | 47.0004 | 87.967
Converge Water Température
[12 empty] | 1.1 | 1.1 | n |  |  | 1.1 | 1.1 | 1.1
[5 empty] | Inj FLOW 1st | 707.3 |  |  | 707.3 | 707.3
JOU flow
F side
[5 empty] | TPTB FLOW 1st | 286.8 |  |  | 286.8 | 286.8
[5 empty] | MAIN FLOW 1st | 255.1 |  |  | 255.1 | 255.1
[5 empty] | SIDE FLOW 1st | 228.8 | 282 |  | 228.8 | 228.8
[5 empty] | OIL FLOW 1st | 1478 | 282 |  | 1478 | 1478
[5 empty] | Total Flow m3/h | 88.68 | 16.92 |  | 88.68 | 88.68
[9 empty] | 29.034 | 29.034
[5 empty] | Total Flow gas | 2546.759 | 371.0875 |  | 1.6354
[5 empty] | Ratio oil/gas | 3.365% | 4.361%
[12 empty] | 8 | 9 | P3 |  |  | 8 | 9 | 9
[12 empty] | 1653030.0121 | 1905015.6089 | kW |  |  | 1653030.0121 | 932055.1829 | 2091279.5668
Viscoity
1 Pa.s = 1 N s/m2 = 1 kg/m.s
The dynamic viscosity is also often expressed in the metric CGS (centimeter-gram-second) system as g/cm.s, dyne.s/cm2 or poise (p) where
1 poise = 1 dyne s/cm2 = 1 g/cm.s = 1/10 Pa.s = 1/10 N.s/m2
For practical use the Poise is to large and it's usual divided by 100 into the smaller unit called the centiPoise (cP) where
1 cP = 0.01 poise = 0.01 gram per cm second = 0.001 Pascal second = 1 milliPascal second = 0.001 N.s/m2
Kinematic Viscosity
is the ratio of absolute or dynamic viscosity to density - a quantity in which no force is involved. Kinematic viscosity can be obtained by dividing the absolute viscosity of a fluid with it's mass density
ν = μ / ρ
ν = kinematic viscosity
μ = absolute or dynamic viscosity
ρ = density
In the SI-system the theoretical unit is m2/s or commonly used Stoke (St) where
1 St (Stokes) = 10-4 m2/s = 1 cm2/s
| 1 cSt (centiStokes) = 10-6 m2/s = 1 mm2/s |  |  |  | 78.87
Conversion from absolute to kinematic viscosity can also be expressed as:
ν = 6.7197 10-4 μ / γ
[6 empty] | LPG46 | RARUS |  | LPG46 | RARUS
|  |  |  | OIL SPEC HT J/kg K 1950 2070 |  | 1950 | 2070 |  | 1950 | 2070
|  |  |  | OIL SPEC WT kg/m3 983 846 |  | 983 | 846 |  | 983 | 846
|  |  |  | P=m.cp.DT=Qv.rho.cP.DT |  | 1916850 | 1751220 |  | 1916850 | 1751220 | 9.458%
[7 empty] | 1.2758 | helium
[7 empty] | Components | Mole Fractions
[7 empty] | helium | 49.59%
[7 empty] | nitrogen | 47.59%
[7 empty] | methane | 1.935%
[7 empty] | argon | 0.029%
[7 empty] | hydrogen | 0.826%
air
[7 empty] | carbon monoxide | 0.003%
[7 empty] | oxygen | 0.023%
[7 empty] | Total | 1
40
25.35
3.853
#NAME?

## Sheet2
| Displacment 1 | 652
Helium | g/s | 1162.8 | 1053.5 | 1164.8 | 1165.8 | 1166.8 | 1167.8 | 1168.8 | 1169.8 | 1170.8 | 1171.8 | 1172.8 | 1173.8 | 1174.8 | 1175.8 | 1176.8
| kg/h | 4186.08 | 3792.6 | 4193.28 | 4196.88 | 4200.48 | 4204.08 | 4207.68 | 4211.28 | 4214.88 | 4218.48 | 4222.08 | 4225.68 | 4229.28 | 4232.88 | 4236.48
Oil | L/min | 1154.5 | 1155.5 | 1156.5 | 1157.5 | 1158.5 | 1159.5 | 1160.5 | 1161.5 | 1162.5 | 1163.5 | 1164.5 | 1165.5 | 1166.5 | 1167.5 | 1168.5
| m3/h | 69.27 | 69.33 | 69.39 | 69.45 | 69.51 | 69.57 | 69.63 | 69.69 | 69.75 | 69.81 | 69.87 | 69.93 | 69.99 | 70.05 | 70.11
densité | kg/m3 | 835.4 | 836.4 | 837.4 | 838.4 | 839.4 | 840.4 | 841.4 | 842.4 | 843.4 | 844.4 | 845.4 | 846.4 | 847.4 | 848.4 | 849.4
| kg/h | 57868.158 | 57987.612 | 58107.186 | 58226.88 | 58346.694 | 58466.628 | 58586.682 | 58706.856 | 58827.15 | 58947.564 | 59068.098 | 59188.752 | 59309.526 | 59430.42 | 59551.434
|  | 6.746% | 6.139% | 6.731% | 6.723% | 6.716% | 6.708% | 6.701% | 6.693% | 6.686% | 6.678% | 6.671% | 6.664% | 6.656% | 6.649% | 6.642%
Helium | g/s | 1162.8 | 1053.5 | 1164.8 | 1165.8 | 1166.8 | 1167.8 | 1168.8 | 1169.8 | 1170.8 | 1171.8 | 1172.8 | 1173.8 | 1174.8 | 1175.8 | 1176.8
| kg/h | 4186.08 | 3792.6 | 4193.28 | 4196.88 | 4200.48 | 4204.08 | 4207.68 | 4211.28 | 4214.88 | 4218.48 | 4222.08 | 4225.68 | 4229.28 | 4232.88 | 4236.48
Oil | L/min | 1801.0342 | 1155.5 | 1156.5 | 1157.5 | 1158.5 | 1159.5 | 1160.5 | 1161.5 | 1162.5 | 1163.5 | 1164.5 | 1165.5 | 1166.5 | 1167.5 | 1168.5
| m3/h | 108.0621 | 69.33 | 69.39 | 69.45 | 69.51 | 69.57 | 69.63 | 69.69 | 69.75 | 69.81 | 69.87 | 69.93 | 69.99 | 70.05 | 70.11
densité | kg/m3 | 835.4 | 836.4 | 837.4 | 838.4 | 839.4 | 840.4 | 841.4 | 842.4 | 843.4 | 844.4 | 845.4 | 846.4 | 847.4 | 848.4 | 849.4
| kg/h | 90275.0383 | 57987.612 | 58107.186 | 58226.88 | 58346.694 | 58466.628 | 58586.682 | 58706.856 | 58827.15 | 58947.564 | 59068.098 | 59188.752 | 59309.526 | 59430.42 | 59551.434
|  | 4.432% | 6.139% | 6.731% | 6.723% | 6.716% | 6.708% | 6.701% | 6.693% | 6.686% | 6.678% | 6.671% | 6.664% | 6.656% | 6.649% | 6.642%
2438.4776

## Sheet3
Maxi
air molar mass | 28.9586
air density | 1.2758 | helium
| Components | Mole Fractions
4.0026 | helium
28.0135 | nitrogen
16.0428 | methane
39.948 | argon
2.0159 | hydrogen
28.9586 | air
28.0101 | carbon monoxide
31.9988 | oxygen
| Total | 0
0
2834.1458
0.54237
2.8805
A - S4
#REF! |  | 49
2940
| Displacment | 6540
Displacment
| Efficiency | 79.9%
| Volumetric flow | 5225.46
16106.9474
| Flow | 2834.1458
| Flow | 787.2627
| Mol Wgt | 4.0026
| Gamma | 1.6689
| Cp | 5.1933
| Pout / Pin | 5.8036
#REF! | T In | 24.6
| P In | 3.36
| P In | 3.36
| P Out | 19.5
| Isothermal Power m.R.T.ln(P2/P1) | 856.1994
| Isothermal Power P.Qv.ln(P2/P1) | 857.6244
| Motor efficiency | 95%
| Overall Power | 1828.5
| Isothermal Efficiency | 46.83%
| Cust max Water Temp | 50
| dT Water/Oil | 0
dT Water/He
#REF! | Tout before after cooler | 85.8
#REF! | T out | 57
| Water Delta T | 10
| Needed Overall Water Flow (Mech Power/DT) | 157.4785
| Water to cool oil | 147.3375
| Water to cool Helium | 10.141
| Tin Oil | 50
| cp oil | 1.95
| Density (kg/m3) | 980
| Kynematic Viscosity (cSt =10-6 m2/s = 1 mm2/s | 9.7784
| Absolute Viscosity (Pa.s = 1 N s/m2 = 1 kg/m.s) | 0.0095828
| T Out Adiab | 329.3446
| DT extracted by oil cooler | 243.5446
| Power extracted by oil | 995.7273
| Needed Oil flow | 52.3961
873.2688
| Power extracted by oil | 1645.65
Flow
| Needed Oil flow | 86.5957
| Needed Oil flow | 1443.2614
0.93125
1443.2614
% Power
| Power T | 995.7273
| Power P | 70.7389
Converge Water Température
| Inj FLOW | 526
| Jou FLOW | -
| F Side FLOW | -
| TPTB FLOW | 319.5
| MAIN FLOW | 284.2
| SIDE FLOW | 254.8
| OIL FLOW | 1384.5
83.07
| Total Flow gas | 983.9218
| Ratio oil/gas | 7.785%
Viscoity
1 Pa.s = 1 N s/m2 = 1 kg/m.s
The dynamic viscosity is also often expressed in the metric CGS (centimeter-gram-second) system as g/cm.s, dyne.s/cm2 or poise (p) where
1 poise = 1 dyne s/cm2 = 1 g/cm.s = 1/10 Pa.s = 1/10 N.s/m2
For practical use the Poise is to large and it's usual divided by 100 into the smaller unit called the centiPoise (cP) where
1 cP = 0.01 poise = 0.01 gram per cm second = 0.001 Pascal second = 1 milliPascal second = 0.001 N.s/m2
Kinematic Viscosity
is the ratio of absolute or dynamic viscosity to density - a quantity in which no force is involved. Kinematic viscosity can be obtained by dividing the absolute viscosity of a fluid with it's mass density
ν = μ / ρ
ν = kinematic viscosity
μ = absolute or dynamic viscosity
ρ = density
In the SI-system the theoretical unit is m2/s or commonly used Stoke (St) where
1 St (Stokes) = 10-4 m2/s = 1 cm2/s
1 cSt (centiStokes) = 10-6 m2/s = 1 mm2/s
Conversion from absolute to kinematic viscosity can also be expressed as:
ν = 6.7197 10-4 μ / γ
LPG46
1950
983
1916850

## 313K002A-B (2)
air molar mass | 28.9586
air density | 1.2758
4.0026
28.0135
16.0428
39.948
2.0159 |  |  | initial 2003 |  | Site
28.9586 |  | Fluid | helium;1 |  | helium
28.0101 |  | Components | Mole Fractions |  | Mole Fractions
31.9988 |  | helium | 100%
|  | nitrogen | 0%
|  | methane | 0%
|  | argon | 0%
|  | hydrogen | 0%
|  | air | 0%
|  | carbon monoxide | 0%
|  | oxygen | 0%
|  | Total | 1 |  | 0
|  | Srew displacement | 6540 |  | 6540
|  | Volumetric Efficiency | 82.2% |  | 80.5%
|  | Volumetric flow | 5376.08 |  | 5264.7
|  |  | 4846.4563 |  | 18154.5078
|  | Flow | 1088.64 |  | 3193.8404
|  | Flow | 302.4 |  | 887.1779
|  | Mol Wgt | 4.0026 |  | 4.0026
|  | Gamma | 1.6673 |  | 1.6692
|  | Cp | 5.1932 |  | 5.1933
|  | Pout / Pin | 4.0952 |  | 5.4083
|  | T In | 45 |  | 33.4
|  | P In | 1.05 |  | 3.87
|  | P In | 1.05 |  | 3.87
|  | P Out | 4.3 |  | 20.93
|  | Isothermal Power m.R.T.ln(P2/P1) | 281.7387 |  | 953.5288
|  | Isothermal Power P.Qv.ln(P2/P1) | 221.0638 |  | 955.2923
|  | Adiabatique Power m.R.T.gamma/(gamma-1)*((P2/P1)^.. | 378.5477 |  | 1363.1153
|  | Motor efficiency | 95% |  | 95%
|  | Overall Power | 479.2 |  | 0
|  | Overall Power | 479.2 |  | 1974.1797
|  | Isothermal Efficiency | 58.79% |  | 48.3%
|  | Adiabatique Efficiency | 79% |  | 69.05%
|  | Cust max Water Temp | 50 |  | 47.3
|  | dT Water/Oil | 0 |  | 0
dT Water/He
|  | Tout before after cooler | 70.5676 |  | 87.9757
|  | T out | 57 |  | 57
Power adiabatique
|  | Water Delta T | 10 |  | 10
|  | Needed Overall Water Flow (Mech Power/DT) | 41.2708 |  | 170.025
|  | Water to cool oil | 39.4358 |  | 157.7337
|  | Water to cool Helium | 1.835 |  | 12.2913
|  | Tin Oil | 50 |  | 47.3
|  | cp oil | 1.95 |  | 1.95
|  | Density (kg/m3) | 980 |  | 980 | Power isotherm
|  | Kynematic Viscosity (cSt =10-6 m2/s = 1 mm2/s | 14.1477 |  | 9.258
|  | Absolute Viscosity (Pa.s = 1 N s/m2 = 1 kg/m.s) | 0.013865 |  | 0.0090728
|  | T Out Adiab | 286.205 |  | 329.9493
|  | DT extracted by oil cooler | 215.6374 |  | 241.9736
|  | Power extracted by oil | 428.6825 |  | 1614.6311
|  | Oil Flow | 39.264 |  | 74.779
|  | Oil Flow | 654.4 |  | 1246.3174
-591.9174
|  | Total Flow gas | 1702.6566 |  | 1025.1273
|  | Ratio oil/gas | 2.306% |  | 7.295%
|  | rho_inlet | 0.1588 |  | 0.60665
|  | rho_outlet | 0.63938 |  | 3.1156
|  | rho_Nm3 | 0.17615
|  | 302 | 6177.2727 | 12354.5455
|  | 257 | 5256.8182 | 10513.6364
|  | 900 | 18393.6085 | 36787.217

## 313K002A-B
air molar mass | 28.9586
air density | 1.2758
4.0026
28.0135
16.0428
39.948 |  |  | initial 2003 |  | Site conditions | Site | Site | Site new oil
2.0159 |  |  |  |  | Without cooler limit | With cooler limit
28.9586 |  | Fluid | helium;1 |  | helium;1 | helium;1 | helium;1 | helium;1
28.0101 |  | Components | Mole Fractions |  | Mole Fractions | Mole Fractions | Mole Fractions | Mole Fractions
31.9988 |  | helium | 100% |  | 100% | 100% | 100% | 100% | Power adiabatique
|  | nitrogen | 0% |  | 0% | 0% | 0% | 0%
|  | methane | 0% |  | 0% | 0% | 0% | 0%
|  | argon | 0% |  | 0% | 0% | 0% | 0%
|  | hydrogen | 0% |  | 0% | 0% | 0% | 0%
|  | air | 0% |  | 0% | 0% | 0% | 0%
|  | carbon monoxide | 0% |  | 0% | 0% | 0% | 0%
|  | oxygen | 0% |  | 0% | 0% | 0% | 0%
|  | Total | 1 |  | 1 | 1 | 1 | 1
|  | Srew displacement | 6540 |  | 6540 | 6540 | 6540 | 6540
|  | Volumetric Efficiency | 82.2% |  | 80.5% | 80.5% | 80.5% | 80.5%
|  | Volumetric flow | 5376.08 |  | 5264.7 | 5264.7 | 5264.7 | 5264.7
|  | Flow Nm3/h | 18416.5339 |  | 18154.5078 | 18154.5078 | 18154.5078 | 18154.5078
|  | Flow kg/h | 3240 |  | 3193.8404 | 3193.8404 | 3193.8404 | 3193.8404
|  | Flow g/s | 900 |  | 887.1779 | 887.1779 | 887.1779 | 887.1779
|  | Mol Wgt | 4.0026 |  | 4.0026 | 4.0026 | 4.0026 | 4.0026
|  | Gamma | 1.6691 |  | 1.6692 | 1.6692 | 1.6692 | 1.6692
|  | Cp | 5.1932 |  | 5.1933 | 5.1933 | 5.1933 | 5.1933
|  | Pout / Pin | 5.381 |  | 5.4083 | 5.4083 | 5.4083 | 5.4083
|  | T In | 45 |  | 33.4 | 33.4 | 33.4 | 33.4
|  | P In | 3.99 |  | 3.87 | 3.87 | 3.87 | 3.87
|  | P In | 3.99 |  | 3.87 | 3.87 | 3.87 | 3.87
|  | P Out | 21.47 |  | 20.93 | 20.93 | 20.93 | 20.93
|  | Isothermal Power m.R.T.ln(P2/P1) | 1000.9017 |  | 953.5288 | 953.5288 | 953.5288 | 953.5288
|  | Isothermal Power P.Qv.ln(P2/P1) | 1002.7334 |  | 955.2923 | 955.2923 | 955.2923 | 955.2923
|  | Adiabatique Power m.R.T.gamma/(gamma-1)*((P2/P1)^.. | 1429.204 |  | 1363.1153 | 1363.1153 | 1363.1153 | 1363.1153
|  | Motor efficiency | 95% |  | 95% | 95% | 95% | 95%
|  | Itensity | 156.2287 |  | 178.9 | 178.9 | 189.7289 | 180
|  | Overall Power | 1625.2 |  | 1861.0425 | 1861.0425 | 1973.692 | 1872.4855
|  | Isothermal Efficiency | 61.59% |  | 51.24% | 51.24% | 48.31% | 50.92%
|  | Adiabatique Efficiency | 87.94% |  | 73.24% | 73.24% | 69.06% | 72.8%
HELIUM COOLER
|  | Water inlet | 46.6 |  | 46.6 | 47.7174 | 46.6 | 46.6
|  | Water supply temp. | 38.9 |  | 38.9 | 38.9 | 38.9 | 38.9
|  | dT Water/Oil | 3.4 |  | 3 | 3 | 3 | 3
dT Water/He
|  | Tout before after cooler (Tin Oil cooler) | 85.4325 |  | 85.6061 | 95.3866 | 100.6217 | 95.2728
|  | T out | 57 |  | 57 | 57 | 57 | 57
|  | Water Delta T | 7.7 |  | 7.7 | 8.8174 | 7.7 | 7.7
|  | Needed Overall Water Flow (Mech Power/DT) | 181.7784 |  | 208.1574 | 181.7784 | 220.7572 | 209.4373
|  | Water to cool oil | 166.9146 |  | 193.4157 | 164.5034 | 198.2776 | 189.7141
|  | Water to cool Helium | 14.8638 |  | 14.7416 | 17.275 | 22.4796 | 19.7232
|  | Tin screw Oil (Oil Tout HX) | 50 |  | 47 | 47 | 47 | 47
|  | cp oil | 1.95 |  | 1.95 | 1.95 | 1.95 | 2.17
|  | Density (kg/m3) | 980 |  | 980 | 980 | 980 | 835
|  | T Out Adiab | 351.4863 |  | 329.9493 | 329.9493 | 329.9493 | 329.9493
|  | DT extracted by oil cooler | 266.0538 |  | 244.3432 | 234.5626 | 229.3276 | 234.6765
|  | Power to be extracted by oil | 1414.0402 |  | 1537.0048 | 1475.4816 | 1529.8697 | 1485.2743
|  | Oil Flow | 75.18 |  | 75 | 75.18 | 75.18 | 75.18
|  | Oil Flow | 1253 |  | 1250 | 1253 | 1253 | 1253
|  | F : Factor for DTML calc. | 0.92256 |  | 0.92256 | 0.92256 | 0.92256 | 0.92256
|  | DTML | 20.43 |  | 18.1395 | 20.596 | 22.3266 | 20.873
|  | UA = UAref x (m/mref) | 69.2139 |  | 84.7327 | 68.2278 | 68.5222 | 71.9483
|  | MARGE surface |  |  | 0% | 5%
|  | P=UA x DTML | 1414.0402 |  | 1537.0048 | 1475.4816 | 1529.8697 | 1501.7773
HX SIZE ??
[5 empty] | 0 | 2.2516e-07 | -9.8813e-06 | -16.503
|  | P |  |  |  | 0.1561
|  | R |  |  |  | 5.4876
|  | Total Flow gas | 987.7223 |  | 998.5294 | 998.5294 | 998.5294 | 998.5294
|  | Ratio oil/gas | 7.611% |  | 7.511% | 7.529% | 7.529% | 7.529%
|  | rho_inlet | 0.60267 |  | 0.60665 | 0.60665 | 0.60665 | 0.60665
|  | rho_outlet | 3.2803 |  | 3.1985 | 3.1985 | 3.1985 | 3.1985
|  | rho_Nm3 | 0.17615
|  | Kynematic Viscosity (cSt =10-6 m2/s = 1 mm2/s | 9.8688 |  | 9.826 | 7.7026 | 6.8518 | 9.0648
|  | Absolute Viscosity (Pa.s = 1 N s/m2 = 1 kg/m.s) | 0.0096715 |  | 0.0096295 | 0.0075485 | 0.0067147 | 0.0075691
|  |  | 0 |  |  | 6699.7531
0.16103
|  | lambda | 0.1451
0.6291
0.11791
|  | P | 2895060 | W |  | 3292958.475 | 3969112.6152
|  | DTML | 20.43 |  |  | 20.43 | 20.43
|  | A | 429.82 | m² |  | 429.82 | 429.82
|  | U | 329.6876 | W/m².K |  | 375 | 452
|  |  | 1.1344 |  |  | 0.0026667 | 0.0022124

## 313K002A-B_avec oil HX et after
Vi = Vs/Vd
air molar mass | 28.9586 | Pi = Vi^k
|  | L | 2.63 | [10 empty] | 2.63
air density | 1.2758 | M | 3.65 | [10 empty] | 3.65
|  | H | 5.8 | [10 empty] | 5.8
|  | Pi = Vi^k | 8.5784 | [10 empty] | 8.5784
4.0026
28.0135
16.0428
39.948 |  |  | initial 2003 |  | Calculations based on site | Calculations based on site | Calculations based on site | Calculations based on site | Calculations based on site | Calculations based on site | Calculations based on site | Calculations based on site | Calculations based on site | design | Site new oil
2.0159 |  |  |  |  | Without He cooler margin | With He cooler margin | With He cooler margin | 313K002A - 2005 | 313K002B - 2005 | 313K002A - 2008-02-04 | 313K002B - 2008-02-04 | 313K002A - 2007 | 313K002A - 2007
28.9586 |  | Fluid | helium;1 |  | helium;1 | helium;1 | helium;1 | helium;1 | helium;1 | helium;1 | helium;1 | helium;1 | helium;1 | helium;1 | helium;1
28.0101 |  | Components | Mole Fractions |  | Mole Fractions | Mole Fractions | Mole Fractions | Mole Fractions | Mole Fractions | Mole Fractions | Mole Fractions | Mole Fractions | Mole Fractions | Mole Fractions | Mole Fractions
31.9988 |  | helium | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | Power adiabatique
|  | nitrogen | 0% |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | methane | 0% |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | argon | 0% |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | hydrogen | 0% |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | air | 0% |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | carbon monoxide | 0% |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | oxygen | 0% |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Total | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Srew displacement | 6540 |  | 6540 | 6540 | 6540 | 6540 | 6540 | 6540 | 6540 | 6540 | 6540 | 6540 | 6540
|  | Volumetric Efficiency | 82.2% |  | 82.2% | 82.2% | 82.2% | 82.2% | 82.2% | 82.2% | 82.2% | 82.2% | 82.2% | 82.2% | 80.5%
|  | Volumetric flow | 5376.08 |  | 5376.08 | 5376.08 | 5376.08 | 5376.08 | 5376.08 | 5376.08 | 5376.08 | 5376.08 | 5376.08 | 5376.08 | 5264.7
|  | Flow Nm3/h | 18416.5339 |  | 18538.5846 | 18538.5846 | 18538.5846 | 14605.1861 | 14556.6639 | 19320.7655 | 19320.7655 | 14520.2313 | 14473.0877 | 4846.4563 | 18154.5078
|  | Flow kg/h | 3240 |  | 3261.4093 | 3261.4093 | 3261.4093 | 2570.3946 | 2561.8671 | 3398.742 | 3398.742 | 2555.4758 | 2547.1904 | 853.745 | 3193.8404
|  | Flow g/s | 900 |  | 905.947 | 905.947 | 905.947 | 713.9985 | 711.6298 | 944.095 | 944.095 | 709.8544 | 707.5529 | 237.1514 | 887.1779
|  | Mol Wgt | 4.0026 |  | 4.0026 | 4.0026 | 4.0026 | 4.0026 | 4.0026 | 4.0026 | 4.0026 | 4.0026 | 4.0026 | 4.0026 | 4.0026
|  | Gamma | 1.6691 |  | 1.6692 | 1.6692 | 1.6692 | 1.6687 | 1.6687 | 1.6693 | 1.6693 | 1.6686 | 1.6686 | 1.6673 | 1.6692
|  | Cp | 5.1932 |  | 5.1933 | 5.1933 | 5.1933 | 5.1933 | 5.1933 | 5.1933 | 5.1933 | 5.1932 | 5.1932 | 5.1932 | 5.1933
|  | Pout / Pin | 5.381 |  | 5.4083 | 5.4083 | 5.4083 | 6.3654 | 6.3933 | 5.3655 | 5.3756 | 6.7208 | 6.7557 | 20.4476 | 5.4083
|  | T In | 45 |  | 33.4 | 33.4 | 33.4 | 29.49 | 29.49 | 26.31 | 26.31 | 38.34 | 38.34 | 45 | 33.4
|  | P In | 3.99 |  | 3.87 | 3.87 | 3.87 | 3.01 | 3 | 3.94 | 3.94 | 3.08 | 3.07 | 1.05 | 3.87
|  | P In | 3.99 |  | 3.87 | 3.87 | 3.87 | 3.01 | 3 | 3.94 | 3.94 | 3.08 | 3.07 | 1.05 | 3.87
|  | P Out | 21.47 |  | 20.93 | 20.93 | 20.93 | 19.16 | 19.18 | 21.14 | 21.18 | 20.7 | 20.74 | 21.47 | 20.93
3.8 |  | CR : Compression Ratio | 5.381 |  | 5.4083 | 5.4083 | 5.4083 | 6.3654 | 6.3933 | 5.3655 | 5.3756 | 6.7208 | 6.7557 | 20.4476
2.2251 |  | Ideal Vi | 2.7407 |  | 2.749 | 2.749 | 2.749 | 3.0319 | 3.0399 | 2.7357 | 2.7388 | 3.1323 | 3.1421 | 6.1105
|  | Choosen Vi = Vs/Vd | 2.63 |  | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 3.65
|  | Internal pressure ratio Pi = Vi ^ gamma | 5.0231 |  | 5.0232 | 5.0232 | 5.0232 | 5.0207 | 5.0207 | 5.0238 | 5.0238 | 5.0206 | 5.0205 | 5.0142 | 8.681
|  | Internal pressure / external pressure | 93.35% |  | 92.88% | 92.88% | 92.88% | 78.87% | 78.53% | 93.63% | 93.46% | 74.7% | 74.32% | 24.52% | 74860.8129
|  | Isothermal Power m.R.T.ln(P2/P1) | 1000.9017 |  | 973.7017 | 973.7017 | 973.7017 | 830.7505 | 829.9498 | 986.5699 | 987.68 | 875.0291 | 874.5646 | 472.9609 | 953.5288
|  | Isothermal Power P.Qv.ln(P2/P1) | 1002.7334 |  | 975.5025 | 975.5025 | 975.5025 | 831.9727 | 831.167 | 988.4738 | 989.5861 | 876.3053 | 875.8362 | 473.2085 | 955.2923
|  | Adiabatique Power m.R.T.gamma/(gamma-1)*((P2/P1)^.. | 1429.204 |  | 1391.9534 | 1391.9534 | 1391.9534 | 1231.497 | 1231.5173 | 1407.9126 | 1410.0906 | 1313.0909 | 1313.9262 | 918.7431 | 1363.1153
38.3 |  | Motor efficiency | 95% |  | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95%
35.86 |  | Itensity | 156.2287 |  | 178.9 | 178.9 | 178.9 | 164.3 | 164.5 | 178.1 | 181.2 | 170.7 | 180.2 | 156.2287 | 180
2.44
|  | Overall Power | 1625.2 |  | 1861.0425 | 1861.0425 | 1861.0425 | 1709.1631 | 1711.2437 | 1852.7204 | 1884.9687 | 1775.7404 | 1874.566 | 1625.2 | 1872.4855
|  | Isothermal Efficiency | 61.59% |  | 52.32% | 52.32% | 52.32% | 48.61% | 48.5% | 53.25% | 52.4% | 49.28% | 46.65% | 29.1% | 50.92%
|  | Adiabatique Efficiency | 87.94% |  | 74.79% | 74.79% | 74.79% | 72.05% | 71.97% | 75.99% | 74.81% | 73.95% | 70.09% | 56.53% | 72.8%
|  | Tout before after cooler (Tin Oil cooler) | 85.8 |  | 91.7008 | 88.4327 | 88.4327 | 81.25 | 82.24 | 88.6 | 89.17 | 88.76 | 87.43 | 85.8 | 95.2728
|  | T out | 45 |  | 43.9939 | 37.5 | 37.5 | 33 | 33 | 29.66 | 29.66 | 42 | 42 | 45 | 57
|  | dT Tout / Water in | 7 |  | 8.3052 | 2.9165 | 2.9165 | 3 | 3 | 3.34 | 3.34 | 2 | 2 | 7
|  | HELIUM AFTER COOLER | [12 empty] | 46.6
|  | Water inlet | 38 |  | 35.6887 | 34.5835 | 34.5835 | 30 | 30 | 26.32 | 26.32 | 40 | 40 | 38 | 38.9
|  | Water outlet | 39 |  | 36.8532 | 35.8267 | 35.8267 | 30.9282 | 30.9441 | 27.8193 | 27.8338 | 40.8943 | 40.8661 | 39
|  | Water Flow | 166 |  | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166
|  | He inlet after cooler | 85.8 |  | 91.7008 | 88.4327 | 88.4327 | 81.25 | 82.24 | 88.6 | 89.17 | 88.76 | 87.43 | 85.8
|  | He outlet after cooler | 45 |  | 43.9939 | 37.5 | 37.5 | 33 | 33 | 29.66 | 29.66 | 42 | 42 | 45
|  | DTML | 20.9477 |  | 24.6559 | 17.1791 | 17.1791 | 16.7818 | 17.0116 | 19.7983 | 19.9272 | 14.4447 | 14.1577 | 20.9477
|  | Power helium after cooler | 190.6952 |  | 224.4529 | 239.6293 | 239.6293 | 178.9099 | 181.9751 | 288.9808 | 291.7755 | 172.3778 | 166.9319 | 50.2481
|  | UA | 9.1034 |  | 9.1034 | 9.1034 | 9.1034 | 9.1034 | 9.1034 | 9.1034 | 9.1034 | 9.1034 | 9.1034 | 2.3987
|  | Margins on surface | 99.15% |  | 0% | 53.23% | 53.23% | 17.11% | 17.51% | 60.34% | 60.84% | 31.09% | 29.52% | 99.15%
|  | P=UA x DTML x margins | 190.6952 |  | 224.4529 | 239.6293 | 239.6293 | 178.9099 | 181.9751 | 288.9808 | 291.7755 | 172.3778 | 166.9319 | 50.2481
|  | Convergence | 0 |  | 2.2982e-08 | 0 | 0 | -1e-06 | -1e-06 | 0 | 0 | 0 | 0 | 0
OIL COOLER
|  | Water inlet | 39 |  | 36.8532 | 35.8267 | 35.8267 | 30.9282 | 30.9441 | 27.8193 | 27.8338 | 40.8943 | 40.8661 | 39
|  | Water outlet | 46.3262 |  | 44.6286 | 43.7088 | 43.7088 | 38.4303 | 38.4335 | 35.3701 | 35.4999 | 48.8201 | 49.2744 | 46.6
|  | Water Flow | 166 |  | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166
|  | Oil inlet | 85.8 |  | 91.7008 | 88.4327 | 88.4327 | 81.25 | 82.24 | 88.6 | 89.17 | 88.76 | 87.43 | 85.8
|  | Oil outlet going through cooler | 50 |  | 46.7347 | 46.8804 | 46.8804 | 44.25 | 43.9384 | 39.5569 | 39.714 | 52.7271 | 54.0807 | 50 | 2.17
|  | Oil injected in screw (mix by-pass & cooled) | 50 |  | 47.25 | 47.25 | 47.25 | 47.97 | 47.97 | 47.73 | 47.73 | 51.32 | 51.32 | 50 | 2.17
|  | cp oil | 1.95 |  | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 835
|  | Density (kg/m3) | 980 |  | 980 | 980 | 980 | 980 | 980 | 980 | 980 | 980 | 980 | 980 | 329.9493
|  | T Out Adiab | 351.4863 |  | 329.9493 | 329.9493 | 329.9493 | 362.2306 | 363.3416 | 314.1707 | 314.616 | 395.1895 | 396.5759 | 791.4762 | 234.6765
|  | DT extracted by oil cooler | 265.6863 |  | 238.2485 | 241.5166 | 241.5166 | 280.9806 | 281.1016 | 225.5707 | 225.446 | 306.4295 | 309.1459 | 705.6762 | 1485.2743
|  | Power to be extracted by oil | 1412.0867 |  | 1498.6667 | 1519.2246 | 1519.2246 | 1445.984 | 1443.5392 | 1455.3779 | 1477.6059 | 1527.6438 | 1620.652 | 1537.3666 | 74.3054
|  | Oil mass Flow | 72819.2543 |  | 72819.2543 | 72819.2543 | 72819.2543 | 72819.2543 | 72819.2543 | 72819.2543 | 72819.2543 | 72819.2543 | 72819.2543 | 79279.756 | 20640.3782
|  | Oil Flow | 74.3054 |  | 74.3054 | 74.3054 | 74.3054 | 74.3054 | 74.3054 | 74.3054 | 74.3054 | 74.3054 | 74.3054 | 80.8977 | 1238.4227
|  | % oil flow by-passing cooler | 0% |  | 1.146% | 0.8894% | 0.8894% | 10.05% | 10.53% | 16.67% | 16.21% | -3.905% | -8.278% | 0%
|  | Oil Flow | 1238.4227 |  | 1224.2317 | 1227.4081 | 1227.4081 | 1113.9119 | 1108.0664 | 1032.0372 | 1037.6948 | 1286.7822 | 1340.9423 | 1348.2952 | 0.92256
|  | F : Factor for DTM calc. | 0.92256 |  | 0.92256 | 0.92256 | 0.92256 | 0.92256 | 0.92256 | 0.92256 | 0.92256 | 0.92256 | 0.92256 | 0.92256 | 20.873
|  | DTM = F x DTML | 20.5586 |  | 21.9796 | 22.2234 | 22.2234 | 23.3072 | 23.3906 | 25.3197 | 25.5663 | 21.3155 | 21.6999 | 20.4725 | 71.3993
|  | UA = UAref x (m/mref) | 68.6858 |  | 67.8987 | 68.0749 | 68.0749 | 61.7801 | 61.4559 | 57.2392 | 57.5529 | 71.3679 | 74.3718 | 75.0943
|  | Margins on surface | 13.23% |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 13.23% | 1490.3181
|  | P=UA x DTML | 1412.0867 |  | 1492.3858 | 1512.8574 | 1512.8574 | 1439.9238 | 1437.4892 | 1449.2783 | 1471.4131 | 1521.2413 | 1613.8597 | 1537.3666 | -5.0438
|  | Convergence | 0 |  | 6.281 | 6.3672 | 6.3672 | 6.0602 | 6.05 | 6.0996 | 6.1927 | 6.4025 | 6.7923 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
3
|  | Total Flow gas | 988.0354 |  | 1013.036 | 1009.717 | 1009.717 | 854.9621 | 851.2891 | 1015.1675 | 1013.3175 | 812.8526 | 808.5969 | 260.3488 | 998.5294
|  | Ratio oil/gas | 7.521% |  | 7.335% | 7.359% | 7.359% | 8.691% | 8.729% | 7.32% | 7.333% | 9.141% | 9.189% | 31.07% | 7.441%
|  | rho_inlet | 0.60267 |  | 0.60665 | 0.60665 | 0.60665 | 0.47812 | 0.47653 | 0.6322 | 0.6322 | 0.47534 | 0.4738 | 0.1588 | 0.60665
|  | rho_outlet | 3.2792 |  | 3.2194 | 3.23 | 3.23 | 3.0064 | 3.0094 | 3.348 | 3.3541 | 3.1438 | 3.1501 | 3.2792 | 3.1985
|  | rho_Nm3 | 0.17615 | [10 empty] | 0.17615
|  | Water TOTAL Delta T | 8.3262 |  | 8.9399 | 9.1253 | 9.1253 | 8.4303 | 8.4335 | 9.0501 | 9.1799 | 8.8201 | 9.2744 | 8.6 | 7.7
|  | Needed Overall Water Flow (Mech Power/DT) | 168.1069 |  | 179.2871 | 175.6445 | 175.6445 | 174.609 | 174.7548 | 176.3121 | 176.8442 | 173.3936 | 174.0774 | 162.7551 | 209.4373
|  | Power coolers | 1602.7819 |  | 1723.1196 | 1758.8539 | 1758.8539 | 1624.894 | 1625.5142 | 1744.3588 | 1769.3814 | 1700.0216 | 1787.5839 | 1587.6147
|  | Power to be extracted | 1625.2 |  | 1861.0425 | 1861.0425 | 1861.0425 | 1709.1631 | 1711.2437 | 1852.7204 | 1884.9687 | 1775.7404 | 1874.566 | 1625.2
|  |  | -22.4181 |  | -137.9229 | -102.1887 | -102.1887 | -84.2692 | -85.7294 | -108.3616 | -115.5873 | -75.7188 | -86.9822 | -37.5853
47
|  | P |  |  | 0.163 | 0.17347 | 0.17347 | 0.16753 | 0.16441 | 0.1489 | 0.14967 | 0.18427 | 0.19918
|  | R |  |  | 10.2575 | 9.6909 | 9.6909 | 9.6379 | 9.7516 | 9.7899 | 9.7136 | 10.0634 | 9.4271
|  | Kynematic Viscosity (cSt =10-6 m2/s = 1 mm2/s | 9.7784 |  | 8.431 | 9.152 | 9.152 | 10.948 | 10.6844 | 9.1136 | 8.9837 | 9.0769 | 9.386 | 9.7784 | 9.0648
|  | Absolute Viscosity (Pa.s = 1 N s/m2 = 1 kg/m.s) | 0.0095828 |  | 0.0082624 | 0.008969 | 0.008969 | 0.010729 | 0.010471 | 0.0089313 | 0.008804 | 0.0088954 | 0.0091983 | 0.0095828 | 0.0075691
|  |  | 0 | [10 empty] | 0
|  |  | 0.1598 | [10 empty] | 0.17471
|  | lambda | 0.1451 | [10 empty] | 0.1451
|  |  | 0.6291 | [10 empty] | 0.6291
|  |  | 0.11791 | [10 empty] | 0.11791
|  | P | 2895060 | W | 3292958.475 | 3292958.475 | 3292958.475 | 3292958.475 | 3292958.475 | 3292958.475 | 3292958.475 | 3292958.475 | 3292958.475 | 2895060
|  | DTML | 20.43 |  | 20.43 | 20.43 | 20.43 | 20.43 | 20.43 | 20.43 | 20.43 | 20.43 | 20.43 | 20.43
|  | A | 429.82 | m² | 429.82 | 429.82 | 429.82 | 429.82 | 429.82 | 429.82 | 429.82 | 429.82 | 429.82 | 429.82
|  | U | 329.6876 | W/m².K | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 329.6876
|  |  | 1.1344 |  | 0.0026667 | 0.0026667 | 0.0026667 | 0.0026667 | 0.0026667 | 0.0026667 | 0.0026667 | 0.0026667 | 0.0026667 | 1.1344

## test
Vi = Vs/Vd
air molar mass | 28.9586 | Pi = Vi^k
|  | L | 2.63 |  | 2.63
air density | 1.2758 | M | 3.65 |  | 3.65
|  | H | 5.8 |  | 5.8
|  | Pi = Vi^k | 8.5784 |  | 8.5784
4.0026
28.0135
16.0428
39.948 |  |  | helium_design |  | air_design
2.0159
28.9586 |  | Fluid | helium;1 |  | air
28.0101 |  | Components | Mole Fractions |  | Mole Fractions
31.9988 |  | helium | 100% |  | 100%
|  | nitrogen | 0% |  | 0%
|  | methane | 0% |  | 0%
|  | argon | 0% |  | 0%
|  | hydrogen | 0% |  | 0%
|  | air | 0% |  | 0%
|  | carbon monoxide | 0% |  | 0%
|  | oxygen | 0% |  | 0%
|  | Total | 1 |  | 1
|  | Srew displacement | 6540 |  | 6540
|  | Volumetric Efficiency | 82.2% |  | 82.2%
|  | Volumetric flow | 5376.08 |  | 5376.08
|  | Flow Nm3/h | 4923.8386 |  | 4923.8386
|  | Flow kg/h | 867.3693 |  | 6279.5101
|  | Flow g/s | 240.9359 |  | 1744.3084
|  | Mol Wgt | 4.0026 |  | 28.9586
|  | Gamma | 1.6673 |  | 1.4009
|  | Cp | 5.1932 |  | 1.0072
|  | Pout / Pin | 4.7619 |  | 4.7619
|  | T In | 40 |  | 40
|  | P In | 1.05 |  | 1.05
|  | P In | 1.05 |  | 1.05
|  | P Out | 5 |  | 5
3.8 |  | CR : Compression Ratio | 4.7619 |  | 4.7619
2.2271 |  | Ideal Vi | 2.5498 |  | 3.0465
|  | Choosen Vi = Vs/Vd | 2.63 |  | 2.63
|  | Internal pressure ratio Pi = Vi ^ gamma | 5.0143 |  | 3.8756
|  | Internal pressure / external pressure | 105.3% |  | 81.39%
|  | Isothermal Power m.R.T.ln(P2/P1) | 244.5831 |  | 244.7445
|  | Isothermal Power P.Qv.ln(P2/P1) | 244.7132 |  | 244.7132
|  | Adiabatique Power m.R.T.gamma/(gamma-1)*((P2/P1)^.. | 339.7046 |  | 308.5363
38.3 |  | Motor efficiency | 95% |  | 95%
35.86 |  | Itensity | 46.1419 |  | 46.1419
2.44
|  | Overall Power | 480 |  | 480
|  | Isothermal Efficiency | 50.95% |  | 50.99%
|  | Adiabatique Efficiency | 70.77% |  | 64.28%
|  | T Out Adiab | 311.6768 |  | 216.3254
|  | Tout before after cooler (Tin Oil cooler) | 85.8 |  | 85.8
|  | T out | 45 |  | 45
|  | dT Tout / Water in | 7 |  | 7
HELIUM AFTER COOLER
|  | Water inlet | 38 |  | 38
|  | Water outlet | 39 |  | 39
|  | Water Flow | 166 |  | 166
|  | He inlet after cooler | 85.8 |  | 85.8
|  | He outlet after cooler | 45 |  | 45
|  | DTML | 20.9477 |  | 20.9477
|  | Power helium after cooler | 51.05 |  | 71.682
|  | UA | 2.437 |  | 3.422
|  | Margins on surface | 99.15% |  | 99.15%
|  | P=UA x DTML x margins | 51.05 |  | 71.682
|  | Convergence | 0 |  | 0
OIL COOLER
|  | Water inlet | 39 |  | 39
|  | Water outlet | 46.6 |  | 46.6
|  | Water Flow | 166 |  | 166
|  | Oil inlet | 85.8 |  | 85.8
|  | Oil outlet going through cooler | 50 |  | 50
|  | Oil injected in screw (mix by-pass & cooled) | 50 |  | 50
|  | cp oil | 1.95 |  | 1.95
|  | Density (kg/m3) | 980 |  | 980
|  | DT extracted by oil cooler | 225.8768 |  | 130.5254
|  | Power to be extracted by oil | 399.3438 |  | 356.7633
|  | Oil mass Flow | 20593.5784 |  | 18397.7644
|  | Oil Flow | 21.0139 |  | 18.7732
|  | % oil flow by-passing cooler | 0% |  | 0%
|  | Oil Flow | 350.2309 |  | 312.8871
|  | F : Factor for DTM calc. | 0.92256 |  | 0.92256
|  | DTM = F x DTML | 20.4725 |  | 20.4725
|  | UA = UAref x (m/mref) | 19.5064 |  | 17.4265
|  | Margins on surface | 13.23% |  | 13.23%
|  | P=UA x DTML | 399.3438 |  | 356.7633
|  | Convergence | 0 |  | 0
|  | Total Flow gas | 1127.39 |  | 1124.5873
|  | Ratio oil/gas | 1.864% |  | 1.669%
|  | rho_inlet | 0.16134 |  | 1.168
|  | rho_outlet | 0.76936 |  | 5.5838
|  | rho_Nm3 | 0.17615 |  | 0.17615
|  | Water TOTAL Delta T | 8.6 |  | 8.6
|  | Needed Overall Water Flow (Mech Power/DT) | 48.0694 |  | 48.0694
|  | Power coolers | 450.3938 |  | 428.4453
|  | Power to be extracted | 480 |  | 480
|  |  | -29.6062 |  | -51.5547
P
R
|  | Kynematic Viscosity (cSt =10-6 m2/s = 1 mm2/s | 9.7784 |  | 9.7784
|  | Absolute Viscosity (Pa.s = 1 N s/m2 = 1 kg/m.s) | 0.0095828 |  | 0.0095828
|  |  | 0 |  | 0
|  |  | 0.045383 |  | 0.040544
|  | lambda | 0.1451 |  | 0.1451
|  |  | 0.6291 |  | 0.6291
|  |  | 0.11791 |  | 0.11791
|  | P | 2895060 | W | 2895060
|  | DTML | 20.43 |  | 20.43
|  | A | 429.82 | m² | 429.82
|  | U | 329.6876 | W/m².K | 329.6876
|  |  | 1.1344 |  | 1.1344

## Off_design air_to helium
Vi = Vs/Vd
air molar mass | 28.9586 | Pi = Vi^k
|  | L | 2.63 |  |  | 2.63 |  | 2.63
air density | 1.2758 | M | 3.65 |  |  | 3.65 |  | 3.65
|  | H | 5.8 |  |  | 5.8 |  | 5.8
|  | Pi = Vi^k | 8.5784 |  |  | 8.5784 |  | 8.5784
4.0026
28.0135
16.0428
39.948 |  |  | air |  | helium off-design air | helium design |  | ammoniac
2.0159
28.9586 |  | Fluid | air |  | helium;1 | helium |  | ammonia
28.0101 |  | Components | Mole Fractions |  | Mole Fractions | Mole Fractions |  | Mole Fractions
31.9988 |  | helium | 100% |  | 100% | 100% |  | 100%
|  | nitrogen | 0% |  | 0% | 0% |  | 0%
|  | methane | 0% |  | 0% | 0% |  | 0%
|  | argon | 0% |  | 0% | 0% |  | 0%
|  | hydrogen | 0% |  | 0% | 0% |  | 0%
|  | air | 0% |  | 0% | 0% |  | 0%
|  | carbon monoxide | 0% |  | 0% | 0% |  | 0%
|  | oxygen | 0% |  | 0% | 0% |  | 0%
|  | Total | 1 |  | 1 | 1 |  | 1
|  | Srew displacement | 6540 |  | 6540 | 6540 |  | 6540
|  | Volumetric Efficiency | 82.2% |  | 82.2% | 82.2% |  | 82.2%
|  | Volumetric flow | 5376.08 |  | 5376.08 | 5376.08 |  | 5376.08
|  | Flow Nm3/h | 4925.2935 |  | 5171.5582 | 4925.2935 |  | 4925.2935
|  | Flow kg/h | 6282.0769 |  | 910.9826 | 867.6232 |  | 3732.1589
|  | Flow g/s | 1745.0214 |  | 253.0507 | 241.0064 |  | 1036.7108
|  | Mol Wgt | 28.9586 |  | 4.0026 | 4.0026 |  | 17.0303
|  | Gamma | 1.4013 |  | 1.6674 | 1.6673 |  | 1.302
|  | Cp | 1.0065 |  | 5.1932 | 5.1932 |  | 2.1635
|  | Pout / Pin | 5 |  | 4.7619 | 5 |  | 5
|  | T In | 25 |  | 25 | 25 |  | 25
|  | P In | 1 |  | 1.05 | 1 |  | 1
|  | P In | 1 |  | 1.05 | 1 |  | 1
|  | P Out | 5 |  | 5 | 5 |  | 5
3.8 |  | CR : Compression Ratio | 5 |  | 4.7619 | 5 |  | 5
2.5926 |  | Ideal Vi | 3.1534 |  | 2.5497 | 2.6255 |  | 3.4423
|  | Choosen Vi = Vs/Vd | 2.63 |  | 2.63 | 2.63 |  | 2.63
|  | Internal pressure ratio Pi = Vi ^ gamma | 3.8771 |  | 5.0145 | 5.0143 |  | 3.5219
|  | Internal pressure / external pressure | 77.54% |  | 105.3% | 100.3% |  | 70.44%
|  | Isothermal Power m.R.T.ln(P2/P1) | 240.4043 |  | 244.5766 | 240.2179 |  | 242.8597
|  | Isothermal Power P.Qv.ln(P2/P1) | 240.3463 |  | 244.7132 | 240.3463 |  | 240.3463
|  | Adiabatique Power m.R.T.gamma/(gamma-1)*((P2/P1)^.. | 305.4024 |  | 339.7 | 337.2618 |  | 294.3969
38.3 |  | Motor efficiency | 95% |  | 95% | 95% |  | 95%
35.86 |  | Itensity | 51.3551 |  | 52.2464 | 51.3153 |  | 51.8796
2.44
|  | Overall Power | 534.2318 |  | 543.5036 | 533.8175 |  | 539.6882
|  | Isothermal Efficiency | 45% |  | 45% | 45% |  | 45%
|  | Adiabatique Efficiency | 57.17% |  | 62.5% | 63.18% |  | 54.55%
|  | Tout before after cooler (Tin Oil cooler) | 80 |  | 87.9115 | 80 |  | 80
|  | T out | 36.1026 |  | 33.449 | 36.1 |  | 36.1026
|  | dT Tout / Water in | 6.1026 |  | 3.449 | 6.1 |  | 6.1026
|  | dT Tout oil / Water in | 3 |  | 3 | 3 |  | 3
|  | dT water inlet/outlet | 10 |  | 10.8694 | 10 |  | 10
HELIUM AFTER COOLER
|  | Water inlet | 30 |  | 30 | 30 |  | 30
|  | Water outlet | 31.7345 |  | 31.61 | 31.2922 |  | 32.3056
|  | dT water | 1.7345 |  | 1.61 | 1.2922 |  | 2.3056
|  | Water Flow | 38.285 |  | 38.285 | 36.6214 |  | 36.7794
|  | He inlet after cooler | 80 |  | 87.9115 | 80 |  | 80
|  | He outlet after cooler | 36.1026 |  | 33.449 | 36.1 |  | 36.1026
|  | DTML | 20.3882 |  | 18.9256 | 20.5087 |  | 20.2285
|  | Power helium to be extracted by after cooler | 77.103 |  | 71.5716 | 54.945 |  | 98.459
|  | UA | 3.7817 |  | 3.7817 | 2.6791 |  | 4.8673
|  | Margins on surface | 0% |  | 0% | 0% |  | 0%
|  | P=UA x DTML x margins | 77.103 |  | 71.5716 | 54.945 |  | 98.459
|  | Convergence |  |  | 8.0795e-06
OIL COOLER
|  | Water inlet | 31.7345 |  | 31.61 | 31.2922 |  | 32.3056
|  | Water outlet | 40 |  | 40.8694 | 40 |  | 40
|  | Water Flow | 38.285 |  | 38.285 | 42.0561 |  | 36.7794
|  | Oil inlet | 80 |  | 87.9115 | 80 |  | 80
|  | Oil outlet going through cooler | 34.7345 |  | 34.61 | 34.2922 |  | 35.3056
|  | Oil injected in screw (mix by-pass & cooled) | 34.7345 |  | 34.61 | 34.2922 |  | 35.3056
|  | cp oil | 1.95 |  | 1.95 | 1.95 |  | 1.95
|  | Density (kg/m3) | 980 |  | 980 | 980 |  | 980
|  | T Out Adiab | 199.5868 |  | 283.6766 | 294.6464 |  | 159.9152
|  | DT extracted by oil cooler | 119.5868 |  | 195.7651 | 214.6464 |  | 79.9152
|  | Power to be extracted by oil | 367.4287 |  | 411.6092 | 425.2193 |  | 328.5912
|  | Oil mass Flow | 14985.5762 |  | 14985.5762 | 17174.7439 |  | 13572.8263
|  | Oil Flow | 15.2914 |  | 15.2914 | 17.5252 |  | 13.8498
|  | % oil flow by-passing cooler | 0% |  | 0% | 0% |  | 0%
|  | Oil Flow | 254.8567 |  | 254.8567 | 292.0875 | 1.1461 | 230.8304
|  | F : Factor for DTM calc. | 0.92256 |  | 0.92256 | 0.92256 |  | 0.92256
|  | DTM = F x DTML | 13.178 |  | 14.7619 | 13.178 |  | 13.178
|  | UA = UAref x (m/mref) | 27.882 |  | 27.882 | 32.2674 | 1.1573 | 24.9348
|  | Margins on surface | 0% |  | 0% | 0% |  | 0%
|  | P=UA x DTML | 367.4287 |  | 411.5923 | 425.2193 |  | 328.5912
|  | Convergence |  |  | 0.016939
0
|  | converge water flow as in serial | -1.0545e-05 |  |  | -5.4347 |  | 1.6338e-06
|  | Total Flow gas | 1098.5507 |  | 1156.1161 | 1099.9437 |  | 1058.4332
|  | Ratio oil/gas | 1.392% |  | 1.323% | 1.593% |  | 1.309%
|  | rho_inlet | 1.1685 |  | 0.16945 | 0.16139 |  | 0.69422
|  | rho_outlet | 5.7185 |  | 0.78797 | 0.78879 |  | 3.5261
|  | rho_Nm3 | 0.17615 |  |  | 0.17615 |  | 0.17615
|  | Water TOTAL Delta T | 10 |  | 10.8694 | 10 |  | 10
|  | Needed Overall Water Flow (Mech Power/DT) | 46.0104 |  | 43.0647 | 45.9747 | 0.91477 | 46.4803
|  | Power coolers | 444.5317 |  | 483.1808 | 480.1644 |  | 427.0502
|  | Power to be extracted | 534.2318 |  | 543.5036 | 533.8175 |  | 539.6882
|  |  | -89.7001 |  | -60.3227 | -53.6531 |  | -112.638
|  | P |  |  | 0.19306
|  | R |  |  | 8.088
|  | Kynematic Viscosity (cSt =10-6 m2/s = 1 mm2/s | 11.2881 |  | 9.273 | 11.2881 |  | 11.2881
|  | Absolute Viscosity (Pa.s = 1 N s/m2 = 1 kg/m.s) | 0.011062 |  | 0.0090875 | 0.011062 |  | 0.011062
|  |  | 0 |  |  | 0 |  | 0
|  |  | 0.064869 |  |  | 0.075072 |  | 0.058012
|  | lambda | 0.1451 |  |  | 0.1451 |  | 0.1451
|  |  | 0.6291 |  |  | 0.6291 |  | 0.6291
|  |  | 0.11791 |  |  | 0.11791 |  | 0.11791
|  | P | 2895060 | W | 3292958.475 | 2895060 |  | 2895060
|  | DTML | 20.43 |  | 20.43 | 20.43 |  | 20.43
|  | A | 429.82 | m² | 429.82 | 429.82 |  | 429.82
|  | U | 329.6876 | W/m².K | 375 | 329.6876 |  | 329.6876
|  |  | 1.1344 |  | 0.0026667 | 1.1344 |  | 1.1344

## Examples
Vi = Vs/Vd
air molar mass | 28.9586 | Pi = Vi^k
|  | L | 2.63 |  | 2.63 | 2.63 |  | 2.63
air density | 1.2758 | M | 3.65 |  | 3.65 | 3.65 |  | 3.65
|  | H | 5.8 |  | 5.8 | 5.8 |  | 5.8
|  | Pi = Vi^k | 8.5784 |  | 8.5784 | 8.5784 |  | 8.5784
4.0026
28.0135 |  |  | RHEA - MYCOM-Technical-2009-09-30
16.0428 |  |  |  |  | see below | see below
39.948 |  |  | Howden WLVi 321/220 22 on 100% Helium at 3550 rpm |  | Kobelco - KS50LVS | Kobelco - KS50LX |  | ammoniac
2.0159 |  |  |  |  | 1637 RPM | 2052 RPM
28.9586 |  | Fluid | helium |  | helium | helium |  | ammonia
28.0101 |  | Components | Mole Fractions |  | Mole Fractions | Mole Fractions |  | Mole Fractions
31.9988 |  | helium | 100% |  | 100% | 100% |  | 100%
|  | nitrogen | 0% |  | 0% | 0% |  | 0%
|  | methane | 0% |  | 0% | 0% |  | 0%
|  | argon | 0% |  | 0% | 0% |  | 0%
|  | hydrogen | 0% |  | 0% | 0% |  | 0%
|  | air | 0% |  | 0% | 0% |  | 0%
|  | carbon monoxide | 0% |  | 0% | 0% |  | 0%
|  | oxygen | 0% |  | 0% | 0% |  | 0%
|  | Total | 1 |  | 1 | 1 |  | 1
|  | Srew displacement | 7575.8549 |  | 10360 | 10958 |  | 6540
|  | Volumetric Efficiency | 90.08% |  | 86.9% | 84.4% |  | 82.2%
|  | Volumetric flow | 6824.3301 |  | 9002.84 | 9248.552 |  | 5376.08
|  | Flow Nm3/h | 6130.8396 |  | 7990.3513 | 31426.5597 |  | 4925.2935
|  | Flow kg/h | 1080 |  | 1407.5805 | 5528.936 |  | 3732.1589
|  | Flow g/s | 300 |  | 390.9946 | 1535.8155 |  | 1036.7108
|  | Mol Wgt | 4.0026 |  | 4.0026 | 4.0026 |  | 17.0303
|  | Gamma | 1.6673 |  | 1.6673 | 1.6691 |  | 1.302
|  | Cp | 5.1932 |  | 5.1932 | 5.1932 |  | 2.1635
|  | Pout / Pin | 3.2577 |  | 3.9048 | 5.2239 |  | 5
|  | T In | 34.85 |  | 50 | 50 |  | 25
|  | P In | 1.013 |  | 1.05 | 4.02 |  | 1
|  | P In | 1.013 |  | 1.05 | 4.02 |  | 1
|  | P Out | 3.3 |  | 4.1 | 21 |  | 5
3.8 |  | CR : Compression Ratio | 3.2577 |  | 3.9048 | 5.2239 |  | 5
2.2271 |  | Ideal Vi | 2.0306 |  | 2.2637 | 2.6925 |  | 3.4423
|  | Choosen Vi = Vs/Vd | 2.63 |  | 2.63 | 2.63 |  | 2.63
|  | Internal pressure ratio Pi = Vi ^ gamma | 5.0142 |  | 5.0141 | 5.0229 |  | 3.5219
|  | Internal pressure / external pressure | 153.9% |  | 128.4% | 96.15% |  | 70.44%
|  | Isothermal Power m.R.T.ln(P2/P1) | 226.6688 |  | 357.5052 | 1704.3033 |  | 242.8597
|  | Isothermal Power P.Qv.ln(P2/P1) | 226.7875 |  | 357.6895 | 1707.3924 |  | 240.3463
|  | Adiabatique Power m.R.T.gamma/(gamma-1)*((P2/P1)^.. | 289.7803 |  | 475.3734 | 2417.5819 |  | 294.3969
38.3 |  | Motor efficiency | 95% |  | 95% | 95% |  | 95%
35.86 |  | Itensity | 39.849 |  | 84.1128 | 400.6653 |  | 51.8796
2.44
|  | Overall Power | 414.537 |  | 875 | 4168.0003 |  | 539.6882
|  | Isothermal Efficiency | 54.68% |  | 40.86% | 40.89% |  | 45%
|  | Adiabatique Efficiency | 69.9% |  | 54.33% | 58% |  | 54.55%
|  | Tout before after cooler (Tin Oil cooler) | 80 |  | 85 | 110 |  | 80
|  | T out | 51.1026 |  | 48 | 48 |  | 36.1026
|  | dT Tout / Water in | 6.1026 |  | 3 | 3 |  | 6.1026
|  | dT Tout oil / Water in | 3 |  | 4 | 4 |  | 3
|  | dT water inlet/outlet | 10 |  | 10 | 10 |  | 10
HELIUM AFTER COOLER
|  | Water inlet | 45 |  | 45 | 45 |  | 30
|  | Water outlet | 46.2534 |  | 45.9163 | 46.2854 |  | 32.3056
|  | dT water | 1.2534 |  | 0.91634 | 1.2854 |  | 2.3056
|  | Water Flow | 30.9361 |  | 70.6111 | 331.3132 |  | 36.7794
|  | He inlet after cooler | 80 |  | 85 | 110 |  | 80
|  | He outlet after cooler | 51.1026 |  | 48 | 48 |  | 36.1026
|  | DTML | 16.1645 |  | 14.0562 | 19.8686 |  | 20.2285
|  | Power helium to be extracted by after cooler | 45.0209 |  | 75.1287 | 494.5002 |  | 98.459
|  | UA | 2.7852 |  | 5.3449 | 24.8885 |  | 4.8673
|  | Margins on surface | 0% |  | 0% | 0% |  | 0%
|  | P=UA x DTML x margins | 45.0209 |  | 75.1287 | 494.5002 |  | 98.459
Convergence
OIL COOLER
|  | Water inlet | 46.2534 |  | 45.9163 | 46.2854 |  | 32.3056
|  | Water outlet | 55 |  | 55 | 55 |  | 40
|  | Water Flow | 30.9361 |  | 70.6111 | 331.3132 |  | 36.7794
|  | Oil inlet | 80 |  | 85 | 110 |  | 80
|  | Oil outlet going through cooler | 49.2534 |  | 49.9163 | 50.2854 |  | 35.3056
|  | Oil injected in screw (mix by-pass & cooled) | 49.2534 |  | 49.9163 | 50.2854 |  | 35.3056
|  | cp oil | 1.95 |  | 2.17 | 2.17 |  | 1.95
|  | Density (kg/m3) | 980 |  | 835 | 835 |  | 980
|  | T Out Adiab | 220.9714 |  | 284.2646 | 353.8015 |  | 159.9152
|  | DT extracted by oil cooler | 140.9714 |  | 199.2646 | 243.8015 |  | 79.9152
|  | Power to be extracted by oil | 314.1819 |  | 744.7446 | 3352.4138 |  | 328.5912
|  | Oil mass Flow | 18864.7611 |  | 35216.4275 | 93136.5606 |  | 13572.8263
|  | Oil Flow | 19.2498 |  | 42.1754 | 111.5408 |  | 13.8498
|  | % oil flow by-passing cooler | 0% |  | 0% | 0% |  | 0%
|  | Oil Flow | 320.8293 |  | 702.9227 | 1859.0132 | 2.191 | 230.8304
|  | F : Factor for DTM calc. | 0.92256 |  | 0.92256 | 0.92256 |  | 0.92256
|  | DTM = F x DTML | 9.5725 |  | 11.9045 | 17.951 |  | 13.178
|  | UA = UAref x (m/mref) | 32.8213 |  | 62.5599 | 186.7534 | 1.9061 | 24.9348
|  | Margins on surface | 0% |  | 0% | 0% |  | 0%
|  | P=UA x DTML | 314.1819 |  | 744.7446 | 3352.4138 |  | 328.5912
Convergence
|  | Oil flow | 11.2592
|  | converge water flow as in serial | -1.1608e-05 |  | 8.0144e-06 | 8.857e-06 |  | 1.6338e-06
|  | Total Flow gas | 2174.5794 |  | 2279.5583 | 1763.219 |  | 1058.4332
|  | Ratio oil/gas | 0.8852% |  | 1.85% | 6.326% |  | 1.309%
|  | rho_inlet | 0.15826 |  | 0.15635 | 0.59782 |  | 0.69422
|  | rho_outlet | 0.49665 |  | 0.61748 | 3.1357 |  | 3.5261
|  | rho_Nm3 | 0.17615 |  | 0.17615 | 0.17615 |  | 0.17615
|  | Water TOTAL Delta T | 10 |  | 10 | 10 |  | 10
|  | Needed Overall Water Flow (Mech Power/DT) | 35.7017 |  | 67.823 | 323.0699 | 1.0411 | 46.4803
[5 empty] | 1130.3828 | 5384.498
|  | Power coolers | 359.2028 |  | 819.8733 | 3846.914 |  | 427.0502
|  | Power to be extracted | 414.537 |  | 875 | 4168.0003 |  | 539.6882
|  |  | -55.3342 |  | -55.1268 | -321.0863 |  | -112.638
P
R
|  | Kynematic Viscosity (cSt =10-6 m2/s = 1 mm2/s | 11.2881 |  | 11.7086 | 7.1034 |  | 11.2881
|  | Absolute Viscosity (Pa.s = 1 N s/m2 = 1 kg/m.s) | 0.011062 |  | 0.0097767 | 0.0059314 |  | 0.011062
|  |  | 0 |  | 0 | 0 |  | 0
|  |  | 0.076361 |  | 0.14555 | 0.43449 |  | 0.058012
|  | lambda | 0.1451 |  | 0.1451 | 0.1451 |  | 0.1451
|  |  | 0.6291 |  | 0.6291 | 0.6291 |  | 0.6291
|  |  | 0.11791 |  | 0.11791 | 0.11791 |  | 0.11791
|  | P | 2895060 | W | 2895060 | 2895060 |  | 2895060
|  | DTML | 20.43 |  | 20.43 | 20.43 |  | 20.43
|  | A | 429.82 | m² | 429.82 | 429.82 |  | 429.82
|  | U | 329.6876 | W/m².K | 329.6876 | 329.6876 |  | 329.6876
|  |  | 1.1344 |  | 1.1344 | 1.1344 |  | 1.1344

## Kaeser
Vi = Vs/Vd
air molar mass | 28.9586 | Pi = Vi^k
|  | L | 2.63 |  | 2.63 | 2.63 |  | 2.63
air density | 1.2758 | M | 3.65 |  | 3.65 | 3.65 |  | 3.65
|  | H | 5.8 |  | 5.8 | 5.8 |  | 5.8
|  | Pi = Vi^k | 8.5784 |  | 8.5784 | 8.5784 |  | 8.5784
4.0026
28.0135 |  |  | RHEA - MYCOM-Technical-2009-09-30
16.0428 |  |  |  |  | see below | see below
39.948 |  |  | KAESER |  | Kaeser_sub atm | Kobelco - KS50LX |  | ammoniac
2.0159 |  |  |  |  | 1637 RPM | 2052 RPM
28.9586 |  | Fluid | helium |  | helium | helium |  | ammonia
28.0101 |  | Components | Mole Fractions |  | Mole Fractions | Mole Fractions |  | Mole Fractions
31.9988 |  | helium | 100% |  | 100% | 100% |  | 100%
|  | nitrogen | 0% |  | 0% | 0% |  | 0%
|  | methane | 0% |  | 0% | 0% |  | 0%
|  | argon | 0% |  | 0% | 0% |  | 0%
|  | hydrogen | 0% |  | 0% | 0% |  | 0%
|  | air | 0% |  | 0% | 0% |  | 0%
|  | carbon monoxide | 0% |  | 0% | 0% |  | 0%
|  | oxygen | 0% |  | 0% | 0% |  | 0%
|  | Total | 1 |  | 1 | 1 |  | 1
|  | Srew displacement | 4651.6133 |  | 4651.6133 | 10958 |  | 6540
7200
1.9544 |  | Volumetric Efficiency | 79.2% |  | 79.2% | 84.4% |  | 82.2%
|  | Volumetric flow | 3684.0777 |  | 3684.0777 | 9248.552 |  | 5376.08
|  | Flow Nm3/h | 3269.7544 |  | 1557.0259 | 31426.5597 |  | 4925.2935
|  | Flow kg/h | 576 |  | 274.3516 | 5528.936 |  | 3732.1589
|  | Flow g/s | 160 |  | 76.2088 | 1535.8155 |  | 1036.7108
|  | Mol Wgt | 4.0026 |  | 4.0026 | 4.0026 |  | 17.0303
|  | Gamma | 1.6673 |  | 1.667 | 1.6691 |  | 1.302
|  | Cp | 5.1932 |  | 5.1932 | 5.1932 |  | 2.1635
|  | Pout / Pin | 14.2857 |  | 10 | 5.2239 |  | 5
|  | T In | 50 |  | 50 | 50 |  | 25
|  | P In | 1.05 |  | 0.5 | 4.02 |  | 1
|  | P In | 1.05 |  | 0.5 | 4.02 |  | 1
|  | P Out | 15 |  | 5 | 21 |  | 5
3.8 |  | CR : Compression Ratio | 14.2857 |  | 10 | 5.2239 |  | 5
2.2271 |  | Ideal Vi | 4.928 |  | 3.9801 | 2.6925 |  | 3.4423
|  | Choosen Vi = Vs/Vd | 2.63 |  | 2.63 | 2.63 |  | 2.63
|  | Internal pressure ratio Pi = Vi ^ gamma | 5.0141 |  | 5.0125 | 5.0229 |  | 3.5219
|  | Internal pressure / external pressure | 35.1% |  | 50.12% | 96.15% |  | 70.44%
|  | Isothermal Power m.R.T.ln(P2/P1) | 285.5963 |  | 117.7857 | 1704.3033 |  | 242.8597
|  | Isothermal Power P.Qv.ln(P2/P1) | 285.7435 |  | 117.8181 | 1707.3924 |  | 240.3463
|  | Adiabatique Power m.R.T.gamma/(gamma-1)*((P2/P1)^.. | 509.5352 |  | 193.3745 | 2417.5819 |  | 294.3969
38.3 |  | Motor efficiency | 95% |  | 95% | 95% |  | 95%
35.86 |  | Itensity | 61.009 |  | 27.7123 | 400.6653 |  | 51.8796
2.44
|  | Overall Power | 634.6584 |  | 288.2824 | 4168.0003 |  | 539.6882
|  | Isothermal Efficiency | 45% |  | 40.86% | 40.89% |  | 45%
|  | Adiabatique Efficiency | 80.28% |  | 67.08% | 58% |  | 54.55%
|  | Tout before after cooler (Tin Oil cooler) | 80 |  | 85 | 110 |  | 80
|  | T out | 36.1026 |  | 48 | 48 |  | 36.1026
|  | dT Tout / Water in | 6.1026 |  | 3 | 3 |  | 6.1026
|  | dT Tout oil / Water in | 3 |  | 4 | 4 |  | 3
|  | dT water inlet/outlet | 10 |  | 10 | 10 |  | 10
HELIUM AFTER COOLER
|  | Water inlet | 30 |  | 45 | 45 |  | 30
|  | Water outlet | 31.7345 |  | 45.9163 | 46.2854 |  | 32.3056
|  | dT water | 1.7345 |  | 0.91634 | 1.2854 |  | 2.3056
|  | Water Flow | 18.1113 |  | 13.7628 | 331.3132 |  | 36.7794
|  | He inlet after cooler | 80 |  | 85 | 110 |  | 80
|  | He outlet after cooler | 36.1026 |  | 48 | 48 |  | 36.1026
|  | DTML | 20.3882 |  | 14.0562 | 19.8686 |  | 20.2285
|  | Power helium to be extracted by after cooler | 36.4747 |  | 14.6433 | 494.5002 |  | 98.459
|  | UA | 1.789 |  | 1.0418 | 24.8885 |  | 4.8673
|  | Margins on surface | 0% |  | 0% | 0% |  | 0%
|  | P=UA x DTML x margins | 36.4747 |  | 14.6433 | 494.5002 |  | 98.459
Convergence
OIL COOLER
|  | Water inlet | 31.7345 |  | 45.9163 | 46.2854 |  | 32.3056
|  | Water outlet | 40 |  | 55 | 55 |  | 40
|  | Water Flow | 62.9365 |  | 25.384 | 331.3132 |  | 36.7794
|  | Oil inlet | 80 |  | 85 | 110 |  | 80
|  | Oil outlet going through cooler | 34.7345 |  | 49.9163 | 50.2854 |  | 35.3056
|  | Oil injected in screw (mix by-pass & cooled) | 34.7345 |  | 49.9163 | 50.2854 |  | 35.3056
|  | cp oil | 1.95 |  | 2.17 | 2.17 |  | 1.95
|  | Density (kg/m3) | 980 |  | 835 | 835 |  | 980
|  | T Out Adiab | 663.6162 |  | 538.7714 | 353.8015 |  | 159.9152
|  | DT extracted by oil cooler | 583.6162 |  | 453.7714 | 243.8015 |  | 79.9152
|  | Power to be extracted by oil | 604.0131 |  | 267.728 | 3352.4138 |  | 328.5912
|  | Oil mass Flow | 24634.6679 |  | 12659.943 | 93136.5606 |  | 13572.8263
|  | Oil Flow | 25.1374 |  | 15.1616 | 111.5408 |  | 13.8498
|  | % oil flow by-passing cooler | 0% |  | 0% | 0% |  | 0%
|  | Oil Flow | 418.9569 |  | 252.6935 | 1859.0132 | 0.60315 | 230.8304
|  | F : Factor for DTM calc. | 0.92256 |  | 0.92256 | 0.92256 |  | 0.92256
|  | DTM = F x DTML | 13.178 |  | 11.9045 | 17.951 |  | 13.178
|  | UA = UAref x (m/mref) | 45.835 |  | 22.4896 | 186.7534 | 0.49067 | 24.9348
|  | Margins on surface | 0% |  | 0% | 0% |  | 0%
|  | P=UA x DTML | 604.0131 |  | 267.728 | 3352.4138 |  | 328.5912
Convergence
|  | converge water flow as in serial | -44.8252 |  | -11.6212 | 8.857e-06 |  | 1.6338e-06
|  | Total Flow gas | 244.8951 |  | 364.4782 | 1763.219 |  | 1058.4332
|  | Ratio oil/gas | 10.26% |  | 4.16% | 6.326% |  | 1.309%
|  | rho_inlet | 0.15635 |  | 0.07447 | 0.59782 |  | 0.69422
|  | rho_outlet | 2.352 |  | 0.75272 | 3.1357 |  | 3.5261
|  | rho_Nm3 | 0.17615 |  | 0.17615 | 0.17615 |  | 0.17615
|  | Water TOTAL Delta T | 10 |  | 10 | 10 |  | 10
|  | Needed Overall Water Flow (Mech Power/DT) | 54.6596 |  | 22.3453 | 323.0699 | 1.136 | 46.4803
[5 empty] | 372.4223 | 5384.498
|  | Power coolers | 640.4878 |  | 282.3713 | 3846.914 |  | 427.0502
|  | Power to be extracted | 634.6584 |  | 288.2824 | 4168.0003 |  | 539.6882
|  |  | 5.8294 |  | -5.9111 | -321.0863 |  | -112.638
P
R
|  | Kynematic Viscosity (cSt =10-6 m2/s = 1 mm2/s | 11.2881 |  | 11.7086 | 7.1034 |  | 11.2881
|  | Absolute Viscosity (Pa.s = 1 N s/m2 = 1 kg/m.s) | 0.011062 |  | 0.0097767 | 0.0059314 |  | 0.011062
|  |  | 0 |  | 0 | 0 |  | 0
|  |  | 0.10664 |  | 0.052323 | 0.43449 |  | 0.058012
|  | lambda | 0.1451 |  | 0.1451 | 0.1451 |  | 0.1451
|  |  | 0.6291 |  | 0.6291 | 0.6291 |  | 0.6291
|  |  | 0.11791 |  | 0.11791 | 0.11791 |  | 0.11791
|  | P | 2895060 | W | 2895060 | 2895060 |  | 2895060
|  | DTML | 20.43 |  | 20.43 | 20.43 |  | 20.43
|  | A | 429.82 | m² | 429.82 | 429.82 |  | 429.82
|  | U | 329.6876 | W/m².K | 329.6876 | 329.6876 |  | 329.6876
|  |  | 1.1344 |  | 1.1344 | 1.1344 |  | 1.1344

## JCI
Vi = Vs/Vd
air molar mass | 28.9586 | Pi = Vi^k
|  | L | 2.63 |  | 2.63 | 2.63 |  | 2.63
air density | 1.2758 | M | 3.65 |  | 3.65 | 3.65 |  | 3.65
|  | H | 5.8 |  | 5.8 | 5.8 |  | 5.8
|  | Pi = Vi^k | 8.5784 |  | 8.5784 | 8.5784 |  | 8.5784
4.0026
28.0135 |  |  | RHEA - MYCOM-Technical-2009-09-30
16.0428 |  |  |  |  | see below | see below
39.948 |  |  | Howden WLVi 321/220 22 on 100% Helium at 3550 rpm |  | Kobelco - KS50LVS | Kobelco - KS50LX |  | ammoniac
2.0159 |  |  |  |  | 1637 RPM | 2052 RPM
28.9586 |  | Fluid | helium |  | helium | helium |  | ammonia
28.0101 |  | Components | Mole Fractions |  | Mole Fractions | Mole Fractions |  | Mole Fractions
31.9988 |  | helium | 100% |  | 100% | 100% |  | 100%
|  | nitrogen | 0% |  | 0% | 0% |  | 0%
|  | methane | 0% |  | 0% | 0% |  | 0%
|  | argon | 0% |  | 0% | 0% |  | 0%
|  | hydrogen | 0% |  | 0% | 0% |  | 0%
|  | air | 0% |  | 0% | 0% |  | 0%
|  | carbon monoxide | 0% |  | 0% | 0% |  | 0%
|  | oxygen | 0% |  | 0% | 0% |  | 0%
|  | Total | 1 |  | 1 | 1 |  | 1
|  | Srew displacement | 7575.8549 |  | 10360 | 10958 |  | 6540
|  | Volumetric Efficiency | 90.08% |  | 86.9% | 84.4% |  | 82.2%
|  | Volumetric flow | 6824.3301 |  | 9002.84 | 9248.552 |  | 5376.08
|  | Flow Nm3/h | 6130.8396 |  | 7990.3513 | 31426.5597 |  | 4925.2935
|  | Flow kg/h | 1080 |  | 1407.5805 | 5528.936 |  | 3732.1589
|  | Flow g/s | 300 |  | 390.9946 | 1535.8155 |  | 1036.7108
|  | Mol Wgt | 4.0026 |  | 4.0026 | 4.0026 |  | 17.0303
|  | Gamma | 1.6673 |  | 1.6673 | 1.6691 |  | 1.302
|  | Cp | 5.1932 |  | 5.1932 | 5.1932 |  | 2.1635
|  | Pout / Pin | 3.2577 |  | 3.9048 | 5.2239 |  | 5
|  | T In | 34.85 |  | 50 | 50 |  | 25
|  | P In | 1.013 |  | 1.05 | 4.02 |  | 1
|  | P In | 1.013 |  | 1.05 | 4.02 |  | 1
|  | P Out | 3.3 |  | 4.1 | 21 |  | 5
3.8 |  | CR : Compression Ratio | 3.2577 |  | 3.9048 | 5.2239 |  | 5
2.2271 |  | Ideal Vi | 2.0306 |  | 2.2637 | 2.6925 |  | 3.4423
|  | Choosen Vi = Vs/Vd | 2.63 |  | 2.63 | 2.63 |  | 2.63
|  | Internal pressure ratio Pi = Vi ^ gamma | 5.0142 |  | 5.0141 | 5.0229 |  | 3.5219
|  | Internal pressure / external pressure | 153.9% |  | 128.4% | 96.15% |  | 70.44%
|  | Isothermal Power m.R.T.ln(P2/P1) | 226.6688 |  | 357.5052 | 1704.3033 |  | 242.8597
|  | Isothermal Power P.Qv.ln(P2/P1) | 226.7875 |  | 357.6895 | 1707.3924 |  | 240.3463
|  | Adiabatique Power m.R.T.gamma/(gamma-1)*((P2/P1)^.. | 289.7803 |  | 475.3734 | 2417.5819 |  | 294.3969
38.3 |  | Motor efficiency | 95% |  | 95% | 95% |  | 95%
35.86 |  | Itensity | 39.849 |  | 84.1128 | 400.6653 |  | 51.8796
2.44
|  | Overall Power | 414.537 |  | 875 | 4168.0003 |  | 539.6882
|  | Isothermal Efficiency | 54.68% |  | 40.86% | 40.89% |  | 45%
|  | Adiabatique Efficiency | 69.9% |  | 54.33% | 58% |  | 54.55%
|  | Tout before after cooler (Tin Oil cooler) | 80 |  | 85 | 110 |  | 80
|  | T out | 51.1026 |  | 48 | 48 |  | 36.1026
|  | dT Tout / Water in | 6.1026 |  | 3 | 3 |  | 6.1026
|  | dT Tout oil / Water in | 3 |  | 4 | 4 |  | 3
|  | dT water inlet/outlet | 10 |  | 10 | 10 |  | 10
HELIUM AFTER COOLER
|  | Water inlet | 45 |  | 45 | 45 |  | 30
|  | Water outlet | 46.2534 |  | 45.9163 | 46.2854 |  | 32.3056
|  | dT water | 1.2534 |  | 0.91634 | 1.2854 |  | 2.3056
|  | Water Flow | 30.9361 |  | 70.6111 | 331.3132 |  | 36.7794
|  | He inlet after cooler | 80 |  | 85 | 110 |  | 80
|  | He outlet after cooler | 51.1026 |  | 48 | 48 |  | 36.1026
|  | DTML | 16.1645 |  | 14.0562 | 19.8686 |  | 20.2285
|  | Power helium to be extracted by after cooler | 45.0209 |  | 75.1287 | 494.5002 |  | 98.459
|  | UA | 2.7852 |  | 5.3449 | 24.8885 |  | 4.8673
|  | Margins on surface | 0% |  | 0% | 0% |  | 0%
|  | P=UA x DTML x margins | 45.0209 |  | 75.1287 | 494.5002 |  | 98.459
Convergence
OIL COOLER
|  | Water inlet | 46.2534 |  | 45.9163 | 46.2854 |  | 32.3056
|  | Water outlet | 55 |  | 55 | 55 |  | 40
|  | Water Flow | 30.9361 |  | 70.6111 | 331.3132 |  | 36.7794
|  | Oil inlet | 80 |  | 85 | 110 |  | 80
|  | Oil outlet going through cooler | 49.2534 |  | 49.9163 | 50.2854 |  | 35.3056
|  | Oil injected in screw (mix by-pass & cooled) | 49.2534 |  | 49.9163 | 50.2854 |  | 35.3056
|  | cp oil | 1.95 |  | 2.17 | 2.17 |  | 1.95
|  | Density (kg/m3) | 980 |  | 835 | 835 |  | 980
|  | T Out Adiab | 220.9714 |  | 284.2646 | 353.8015 |  | 159.9152
|  | DT extracted by oil cooler | 140.9714 |  | 199.2646 | 243.8015 |  | 79.9152
|  | Power to be extracted by oil | 314.1819 |  | 744.7446 | 3352.4138 |  | 328.5912
|  | Oil mass Flow | 18864.7611 |  | 35216.4275 | 93136.5606 |  | 13572.8263
|  | Oil Flow | 19.2498 |  | 42.1754 | 111.5408 |  | 13.8498
|  | % oil flow by-passing cooler | 0% |  | 0% | 0% |  | 0%
|  | Oil Flow | 320.8293 |  | 702.9227 | 1859.0132 | 2.191 | 230.8304
|  | F : Factor for DTM calc. | 0.92256 |  | 0.92256 | 0.92256 |  | 0.92256
|  | DTM = F x DTML | 9.5725 |  | 11.9045 | 17.951 |  | 13.178
|  | UA = UAref x (m/mref) | 32.8213 |  | 62.5599 | 186.7534 | 1.9061 | 24.9348
|  | Margins on surface | 0% |  | 0% | 0% |  | 0%
|  | P=UA x DTML | 314.1819 |  | 744.7446 | 3352.4138 |  | 328.5912
Convergence
|  | Oil flow | 11.2592
|  | converge water flow as in serial | -1.1608e-05 |  | 8.0144e-06 | 8.857e-06 |  | 1.6338e-06
|  | Total Flow gas | 2174.5794 |  | 2279.5583 | 1763.219 |  | 1058.4332
|  | Ratio oil/gas | 0.8852% |  | 1.85% | 6.326% |  | 1.309%
|  | rho_inlet | 0.15826 |  | 0.15635 | 0.59782 |  | 0.69422
|  | rho_outlet | 0.49665 |  | 0.61748 | 3.1357 |  | 3.5261
|  | rho_Nm3 | 0.17615 |  | 0.17615 | 0.17615 |  | 0.17615
|  | Water TOTAL Delta T | 10 |  | 10 | 10 |  | 10
|  | Needed Overall Water Flow (Mech Power/DT) | 35.7017 |  | 67.823 | 323.0699 | 1.0411 | 46.4803
[5 empty] | 1130.3828 | 5384.498
|  | Power coolers | 359.2028 |  | 819.8733 | 3846.914 |  | 427.0502
|  | Power to be extracted | 414.537 |  | 875 | 4168.0003 |  | 539.6882
|  |  | -55.3342 |  | -55.1268 | -321.0863 |  | -112.638
P
R
|  | Kynematic Viscosity (cSt =10-6 m2/s = 1 mm2/s | 11.2881 |  | 11.7086 | 7.1034 |  | 11.2881
|  | Absolute Viscosity (Pa.s = 1 N s/m2 = 1 kg/m.s) | 0.011062 |  | 0.0097767 | 0.0059314 |  | 0.011062
|  |  | 0 |  | 0 | 0 |  | 0
|  |  | 0.076361 |  | 0.14555 | 0.43449 |  | 0.058012
|  | lambda | 0.1451 |  | 0.1451 | 0.1451 |  | 0.1451
|  |  | 0.6291 |  | 0.6291 | 0.6291 |  | 0.6291
|  |  | 0.11791 |  | 0.11791 | 0.11791 |  | 0.11791
|  | P | 2895060 | W | 2895060 | 2895060 |  | 2895060
|  | DTML | 20.43 |  | 20.43 | 20.43 |  | 20.43
|  | A | 429.82 | m² | 429.82 | 429.82 |  | 429.82
|  | U | 329.6876 | W/m².K | 329.6876 | 329.6876 |  | 329.6876
|  |  | 1.1344 |  | 1.1344 | 1.1344 |  | 1.1344

## JCI (2)
Vi = Vs/Vd
air molar mass | 28.9586 | Pi = Vi^k
|  | L | 2.63 |  | 2.63
air density | 1.2758 | M | 3.65 |  | 3.65
|  | H | 5.8 |  | 5.8
|  | Pi = Vi^k | 8.5784 |  | 8.5784
4.0026
28.0135 |  |  | RHEA - MYCOM-Technical-2009-09-30 |  | RHEA - MYCOM-Technical-2009-09-30
16.0428
39.948 |  |  | KS50LX |  | KS50LVS
2.0159
28.9586 |  | Fluid | helium |  | helium
28.0101 |  | Components | Mole Fractions |  | Mole Fractions
31.9988 |  | helium | 100% |  | 100%
|  | nitrogen | 0% |  | 0%
|  | methane | 0% |  | 0%
|  | argon | 0% |  | 0%
|  | hydrogen | 0% |  | 0%
|  | air | 0% |  | 0%
|  | carbon monoxide | 0% |  | 0%
|  | oxygen | 0% |  | 0%
|  | Total | 1 |  | 1
|  | Srew displacement @ 2950 RPM | 18665.237 |  | 21483.9096
|  | Screw speed | 2052 |  | 1637
|  | Volumetric Efficiency | 84.4% |  | 86.9%
|  | Volumetric flow | 10958 |  | 10360
|  | Flow Nm3/h | 37235.2603 |  | 9194.8807
|  | Flow kg/h | 6550.872 |  | 1619.7704
|  | Flow g/s | 1819.6867 |  | 449.9362
|  | Mol Wgt | 4.0026 |  | 4.0026
|  | Gamma | 1.6691 |  | 1.6673
|  | Cp | 5.1932 |  | 5.1932
|  | Pout / Pin | 5.2239 |  | 3.9048
|  | T In | 50 |  | 50
|  | P In | 4.02 |  | 1.05
|  | P In | 4.02 |  | 1.05
|  | P Out | 21 |  | 4.1
3.8 |  | CR : Compression Ratio | 5.2239 |  | 3.9048
2.2252 |  | Ideal Vi | 2.6925 |  | 2.2637
|  | Choosen Vi = Vs/Vd | 2.63 |  | 2.63
|  | Internal pressure ratio Pi = Vi ^ gamma | 5.0229 |  | 5.0141
|  | Internal pressure / external pressure | 96.15% |  | 128.4%
|  | Isothermal Power m.R.T.ln(P2/P1) | 2019.3167 |  | 411.3984
|  | Isothermal Power P.Qv.ln(P2/P1) | 2022.9768 |  | 411.6105
|  | Adiabatique Power m.R.T.gamma/(gamma-1)*((P2/P1)^.. | 2864.4335 |  | 547.035
38.3 |  | Motor efficiency | 95% |  | 95%
35.86 |  | Itensity | 400.6653 |  | 84.1128
2.44
|  | Overall Power | 4168 |  | 875
|  | Isothermal Efficiency | 48.54% |  | 47.04%
|  | Adiabatique Efficiency | 68.72% |  | 62.52%
|  | Tout before after cooler (Tin Oil cooler) | 110 |  | 85
|  | T out | 52.1026 |  | 52.1026
|  | dT Tout / Water in | 6.1026 |  | 6.1026
|  | dT Tout oil / Water in | 3 |  | 3
|  | dT water inlet/outlet | 10 |  | 10
HELIUM AFTER COOLER
|  | Water inlet | 46 |  | 46
|  | Water outlet | 47.4031 |  | 46.9356
|  | dT water | 1.4031 |  | 0.93558
|  | Water Flow | 335.846 |  | 70.7604
|  | He inlet after cooler | 110 |  | 85
|  | He outlet after cooler | 52.1026 |  | 52.1026
|  | DTML | 24.2673 |  | 17.4601
|  | Power helium to be extracted by after cooler | 547.131 |  | 76.868
|  | UA | 22.546 |  | 4.4025
|  | Margins on surface | 0% |  | 0%
|  | P=UA x DTML x margins | 547.131 |  | 76.868
OIL COOLER
|  | Water inlet | 47.4031 |  | 46.9356
|  | Water outlet | 56 |  | 56
|  | Water Flow | 335.8459 |  | 70.7609
|  | Oil inlet | 110 |  | 85
|  | Oil outlet going through cooler | 50.4031 |  | 49.9356
|  | Oil injected in screw (mix by-pass & cooled) | 50.4031 |  | 49.9356
|  | cp oil | 2.17 |  | 2.17
|  | Density (kg/m3) | 835 |  | 835
|  | T Out Adiab | 353.8015 |  | 284.2646
|  | DT extracted by oil cooler | 243.8015 |  | 199.2646
|  | Power to be extracted by oil | 3352.4136 |  | 744.7446
|  | Oil mass Flow | 93320.3639 |  | 35235.7452
|  | Oil Flow | 111.7609 |  | 42.1985
|  | % oil flow by-passing cooler | 0% |  | 0%
|  | Oil Flow | 1862.6819 |  | 703.3083
|  | F : Factor for DTM calc. | 0.92256 |  | 0.92256
|  | DTM = F x DTML | 16.2783 |  | 10.5728
|  | UA = UAref x (m/mref) | 205.9438 |  | 70.4394
|  | Margins on surface | 0% |  | 0%
|  | P=UA x DTML | 3352.4136 |  | 744.7446
Convergence
|  | Oil flow | 11.2592 |  | 11.2592
|  | converge water flow as in serial | 9.1125e-06 |  | -0.00050128
|  | Total Flow gas | 2096.3564 |  | 2631.5598
|  | Ratio oil/gas in volume | 5.061% |  | 1.578%
|  | rho_inlet | 0.59782 |  | 0.15635
|  | rho_outlet | 3.1249 |  | 0.61552
|  | rho_Nm3 | 0.17615 |  | 0.17615
|  | Water TOTAL Delta T | 10 |  | 10
|  | Needed Overall Water Flow (Mech Power/DT) | 358.9665 |  | 75.3589
|  | Power coolers | 3899.5446 |  | 821.6126
|  | Power to be extracted | 4168 |  | 875
|  |  | -268.4554 |  | -53.3874
P
R
|  | Kynematic Viscosity (cSt =10-6 m2/s = 1 mm2/s | 7.1034 |  | 11.7086
|  | Absolute Viscosity (Pa.s = 1 N s/m2 = 1 kg/m.s) | 0.0059314 |  | 0.0097767
|  |  | 0 |  | 0
|  |  | 0.47914 |  | 0.16388
|  | lambda | 0.1451 |  | 0.1451
|  |  | 0.6291 |  | 0.6291
|  |  | 0.11791 |  | 0.11791
|  | P | 2895060 | W | 2895060
|  | DTML | 20.43 |  | 20.43
|  | A | 429.82 | m² | 429.82
|  | U | 329.6876 | W/m².K | 329.6876
|  |  | 1.1344 |  | 1.1344