## Sheet1
CONTROL VALVE SIZING: LIQUID |  |  | TAG: | PV123 |  |  |  | Jon Monsen |  | Valve sizing per ISA S75.01.01 2012
Flow | gpm | Q | 470 | 470 | 470 | 470 | Valve type |  | Valve style SPL code | DESCRIPTION OF VARIABLE | Eqn. | NAME OF VARIABLE | FORMULA
Inlet pressure | psiA | P_1 | 100 | 100 | 100 | 100 | Globe |  | 0 | CALCULATED IN COLUMN "S" |  | CALCULATED IN COLUMN "S"
Pressure drop | psi | DELTA_P | 15 | 15 | 15 | 15 | Rotary eccentric plug |  | 1 | Critical pressure ratio factor | 4 | F_F | 0.95506 | 0.95506 | 0.95506 | 0.95506
Specific gravity (r1/r0) |  | G | 1 | 1 | 1 | 1 | Segment ball |  | 2 | WITHOUT REDUCERS
Vapor pressure | psiA | P_V | 1 | 1 | 1 | 1 | Butterfly |  | 3 | C Non choked | 1 | C_NonCh | 121.3535 | 121.3535 | 121.3535 | 121.3535
Critical pressure | psiA | P_C | 3208 | ======> | ======> | ======> | Full ball |  | 4 | C Choked | 1 | C_Ch | 62.9681 | 62.9681 | 62.9681 | 62.9681
Recovery factor |  | F_L | 0.75 | 0.75 | 0.75 | 0.75 |  |  |  | Choked pressure drop | 3 | Delta_P_Ch | 55.7128 | 55.7128 | 55.7128 | 55.7128
Inlet pipe diameter | inch | D_1 | 3 | ======> | ======> | ======> |  |  |  | Select C Non choked or C choked | 2 | Applicable_C_NonCh_or_Ch | 121.3535 | 121.3535 | 121.3535 | 121.3535
Outlet pipe diameter | inch | D_2 | 3 | ======> | ======> | ======> |  |  |  | (This is the initial guess for
Valve size | inch | d | 3 | ======> | ======> | ======> |  |  |  | the following iterative calculations)
Valve style SPL code |  | VSC | 2 | ======> | ======> | ======>
Pipe wall correction | dB(A) | DeltaLp | -2 | ======> | ======> | ======> |  |  |  | WITH REDUCERS
Turbulent flow coef. (Cv or Kv) | Cv | C_ | 121.3535 | 121.3535 | 121.3535 | 121.3535 |  |  |  | Reducer velocity head coefficients | 18 | ZETA_1 | 0
Turbulent Flow Calc from Cv or Kv | gpm |  | 470 | 470 | 470 | 470 |  |  |  |  | 17 | ZETA_B1 | 0
Choked delta p | psi |  | 55.7128 | 55.7128 | 55.7128 | 55.7128 |  |  |  |  | 19 | ZETA_2 | 0
Sound pressure level | dB(A) |  | 52.6022 | 52.6022 | 52.6022 | 52.6022 |  |  |  |  | 17 | ZETA_B2 | 0
Valve inlet velocity | ft/s |  | 21.3328 | 21.3328 | 21.3328 | 21.3328 |  |  |  | Sum of velocity head coefficients | 16 | SIGMA_ZETA | 0
Selected valve style (VSC) |  |  | Segment ball | [6 empty] | Sum of upstream velocity head coef |  | SIGMA_ZETA_1 | 0
For non-turbulent flow (valve Reynolds Number < 10,000)
Kinematic viscosity | cS | v | 1000 | 1000 | 1000 | 1000 |  |  |  | Beginning of iterative calculation
Valve style modifier |  | F_D | 0.97 | 0.97 | 0.97 | 0.97 |  |  |  | Assumed C for iterative purposes |  | C_i | 121.3535 | 121.3535 | 121.3535 | 121.3535
Reduced trim? C(Rated)<N18*0.016 (yes or no) |  | RED_TRM | No | ======> | ======> | ======> |  |  |  | Piping geometry factor | 15 | F_P | 1 | 1 | 1 | 1
Valve Reynolds Number |  |  | 750.2454 | 750.2454 | 750.2454 | 750.2454 |  |  |  | Combined liquid pressure recovery
Non-turb flow coef. (Cv or Kv) | Cv |  | 161.6865 | 161.6865 | 161.6865 | 161.6865 |  |  |  | factor and piping geometry factor | 21 | F_LP | 0.75 | 0.75 | 0.75 | 0.75
Non-turb. Flow Calc from Cv or Kv | gpm |  | 470 | 470 | 470 | 470 |  |  |  | C Non choked w/ reducers | 1 | C_NonCh_W_Reducers | 121.3535 | 121.3535 | 121.3535 | 121.3535
[6 empty] | Data input |  |  |  | C Choked w/ reducers | 1 | C_Ch_W_Reducers | 62.9681 | 62.9681 | 62.9681 | 62.9681
[6 empty] | Final results |  |  |  | Choked pressure drop w/ reducers | 3 | Delta_P_Ch_W_Reducers | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
Numerical constants | [9 empty] | Ci/ C, this iteration |  | C_i divided by S29 | 1 | 1 | 1 | 1
N_1 | 1
N_2 | 890 | [8 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
N_4 | 17300 | [8 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
N_18 | 645 | [8 empty] | Combined liquid pressure recovery
N_32 | 17 | [8 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
N_41 | 12.1 | 12.1=density lbm/ft^3, pressure psia | [7 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
|  | 39.0 =density kg/m^3, barA | [7 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
|  | 3.0=density kg/m^3, pressure kPaA | [7 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
FLAG_1 | 1 | 1=flow coef is Cv 2=flow coef is Kv | [7 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
FLAG_3 | 1 | 1=flow is gpm, valve size is inch, inlet velocity is ft/s | [7 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
2= flow is m^3/h, valve size is mm, inlet velocity is m/s
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
FLAG_1 & N_41 only have an effect in the noise calculation | [9 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
FLAG_3 only has an effect of the Inlet velocity calculation | [9 empty] | Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
This worksheet is distributed at no cost on an as-is basis. | [9 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
The author does not assume any liability for its use. | [9 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
| The cells below (Rows 52 & 54) detrmine if any input data is missing. | [8 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
| If it is, error messages are blanked out of the calculated results. | [8 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
| TURB1 | TURB2 | TURB3 | TURB4
| -91596420000 | -91596420000 | -91596420000 | -91596420000 | [5 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
| N_TURB1 | N_TURB2 | N_TURB3 | N_TURB4 | [5 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
| -88848527400000 | -88848527400000 | -88848527400000 | -88848527400000 | [5 empty] | Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | CI / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor |  |  | 1 | 1 | 1 | 1
[10 empty] | Combined liquid pressure recovery | 15
[10 empty] | factor and piping geometry factor |  |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 21 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 1 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked | 3 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 |  | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | C Non choked w/ reducers | 1 |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | C Choked w/ reducers | 1 |  | 62.9681 | 62.9681 | 62.9681 | 62.9681
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Select C Non choked or C choked |  |  | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
Confirmation that the calculated C will
produce the given flow rate
[10 empty] | Final C calculated above |  | Final_Calculated_C | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Piping geometry factor | 15 | Final_F_P | 1 | 1 | 1 | 1
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 | Final_F_LP | 0.75 | 0.75 | 0.75 | 0.75
[10 empty] | Flow Non choked w/ reducers | 1 | Final_Flow_NonCh_W_Reducers | 470 | 470 | 470 | 470
[10 empty] | Flow Choked w/ reducers | 1 | Final_Flow_Ch_W_Reducers | 905.7944 | 905.7944 | 905.7944 | 905.7944
[10 empty] | Choked pressure drop w/ reducers | 3 | Final_Delta_P_Ch_W_Reducers | 55.7128 | 55.7128 | 55.7128 | 55.7128
[10 empty] | Calculated flow from final calculated C |  | Calc_Flow_From_Final_ Calc_C | 470 | 470 | 470 | 470
Hydrodynamic noise calculation
Based on VDMA24422 1979
[10 empty] | Valve nominal size in inches |  | d_in | 3 | 3 | 3 | 3
[10 empty] | Cv/nominal size in inches squared |  | C_d | 13.4837 | 13.4837 | 13.4837 | 13.4837
VALVE STYLE SPECIFIC
PRESSURE DROP RATIOS WHERE
CAVITATION NOISE IS FIRST
DETECTED
[10 empty] | For globe valves |  | z_0 | 0.299 | 0.299 | 0.299 | 0.299
[10 empty] | For eccentric rotary plug valves |  | z_1 | 0.27979 | 0.27979 | 0.27979 | 0.27979
[10 empty] | For segment ball valves |  | z_2 | 0.29789 | 0.29789 | 0.29789 | 0.29789
[10 empty] | For butterfly valves |  | z_3 | 0.24977 | 0.24977 | 0.24977 | 0.24977
[10 empty] | For ball valves |  | z_4 | 0.30838 | 0.30838 | 0.30838 | 0.30838
[10 empty] | For selected valve based on VSC |  | z | 0.29789 | 0.29789 | 0.29789 | 0.29789
(Valve Style Code)
[10 empty] | Pressure drop ratio |  | x_F | 0.15152 | 0.15152 | 0.15152 | 0.15152
[10 empty] | Scaled pressure drop ratio |  | x_R | 0 | 0 | 0 | 0
VALVE STYLE SPECIFIC NOISE
COEFFICIENT
[10 empty] | For globe valves |  | DeltaLf_0 | -1.1 | -1.1 | -1.1 | -1.1
[10 empty] | For eccentric rotary plug valves |  | DeltaLf_1 | -1.1 | -1.1 | -1.1 | -1.1
[10 empty] | For segment ball valves |  | DeltaLf_2 | 0 | 0 | 0 | 0
[10 empty] | For butterfly valves |  | DeltaLf_3 | 0 | 0 | 0 | 0
[10 empty] | For ball valves |  | DeltaLf_4 | 0 | 0 | 0 | 0
[10 empty] | For selected valve based on VSC |  | DeltaLf | 0 | 0 | 0 | 0
(Valve Style Code)
[10 empty] | Common portion of SPL Calculation |  | SPL_C | 57.8871 | 57.8871 | 57.8871 | 57.8871
[10 empty] | SPL calculation if x_F is <=z |  | SPL_L | 52.6022 | 52.6022 | 52.6022 | 52.6022
[10 empty] | SPL calculation if x_F is >z |  | SPL_G | #NUM! | #NUM! | #NUM! | #NUM!
[10 empty] | Selected SPL (SPL_L or SPL_G) |  | SPL_SELECTED | 52.6022 | 52.6022 | 52.6022 | 52.6022
Non-Turbulent Calculation of C
[10 empty] | Initial value of C for Non-turb Calculations |  | C_i_NT | 121.3535 | 121.3535 | 121.3535 | 121.3535
[10 empty] | Valve Reynolds Number | 23 | Re_V | 849.5105 | 849.5105 | 849.5105 | 849.5105
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 4.8952 | 4.8952 | 4.8952 | 4.8952
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 97.3065 | 97.3065 | 97.3065 | 97.3065
[10 empty] | Select Eta, full or reduced trim |  |  | 4.8952 | 4.8952 | 4.8952 | 4.8952
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 0.79426 | 0.79426 | 0.79426 | 0.79426
[10 empty] | Selected based on actual Rev |  |  | 0.79426 | 0.79426 | 0.79426 | 0.79426
[10 empty] | Calculated flow from Initial Cv | A.2 |  | 373.3013 | 373.3013 | 373.3013 | 373.3013
[10 empty] | Assumed C for iterative purposes |  |  | 152.7885 | 152.7885 | 152.7885 | 152.7885
[10 empty] | Valve Reynolds Number | 23 |  | 768.2594 | 768.2594 | 768.2594 | 768.2594
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 3.0881 | 3.0881 | 3.0881 | 3.0881
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 113.2917 | 113.2917 | 113.2917 | 113.2917
[10 empty] | Select Eta, full or reduced trim |  |  | 3.0881 | 3.0881 | 3.0881 | 3.0881
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 0.75973 | 0.75973 | 0.75973 | 0.75973
[10 empty] | Selected based on actual Rev |  |  | 0.75973 | 0.75973 | 0.75973 | 0.75973
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 449.5686 | 449.5686 | 449.5686 | 449.5686
[10 empty] | Change from previouse iteration |  |  | 20.43% | 20.43% | 20.43% | 20.43%
[10 empty] | Assumed C for iterative purposes |  |  | 159.7322 | 159.7322 | 159.7322 | 159.7322
[10 empty] | Valve Reynolds Number | 23 |  | 754.0516 | 754.0516 | 754.0516 | 754.0516
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 2.8255 | 2.8255 | 2.8255 | 2.8255
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 116.6686 | 116.6686 | 116.6686 | 116.6686
[10 empty] | Select Eta, full or reduced trim |  |  | 2.8255 | 2.8255 | 2.8255 | 2.8255
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 0.75254 | 0.75254 | 0.75254 | 0.75254
[10 empty] | Selected based on actual Rev |  |  | 0.75254 | 0.75254 | 0.75254 | 0.75254
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 465.5544 | 465.5544 | 465.5544 | 465.5544
[10 empty] | Change from previouse iteration |  |  | 3.556% | 3.556% | 3.556% | 3.556%
[10 empty] | Assumed C for iterative purposes |  |  | 161.2575 | 161.2575 | 161.2575 | 161.2575
[10 empty] | Valve Reynolds Number | 23 |  | 751.074 | 751.074 | 751.074 | 751.074
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 2.7723 | 2.7723 | 2.7723 | 2.7723
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 117.4038 | 117.4038 | 117.4038 | 117.4038
[10 empty] | Select Eta, full or reduced trim |  |  | 2.7723 | 2.7723 | 2.7723 | 2.7723
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 0.75099 | 0.75099 | 0.75099 | 0.75099
[10 empty] | Selected based on actual Rev |  |  | 0.75099 | 0.75099 | 0.75099 | 0.75099
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 469.0262 | 469.0262 | 469.0262 | 469.0262
[10 empty] | Change from previouse iteration |  |  | 0.7457% | 0.7457% | 0.7457% | 0.7457%
[10 empty] | Assumed C for iterative purposes |  |  | 161.5923 | 161.5923 | 161.5923 | 161.5923
[10 empty] | Valve Reynolds Number | 23 |  | 750.427 | 750.427 | 750.427 | 750.427
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 2.7608 | 2.7608 | 2.7608 | 2.7608
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 117.5649 | 117.5649 | 117.5649 | 117.5649
[10 empty] | Select Eta, full or reduced trim |  |  | 2.7608 | 2.7608 | 2.7608 | 2.7608
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 0.75064 | 0.75064 | 0.75064 | 0.75064
[10 empty] | Selected based on actual Rev |  |  | 0.75064 | 0.75064 | 0.75064 | 0.75064
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 469.7864 | 469.7864 | 469.7864 | 469.7864
[10 empty] | Change from previouse iteration |  |  | 0.1621% | 0.1621% | 0.1621% | 0.1621%
[10 empty] | Assumed C for iterative purposes |  |  | 161.6658 | 161.6658 | 161.6658 | 161.6658
[10 empty] | Valve Reynolds Number | 23 |  | 750.2853 | 750.2853 | 750.2853 | 750.2853
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 2.7583 | 2.7583 | 2.7583 | 2.7583
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 117.6002 | 117.6002 | 117.6002 | 117.6002
[10 empty] | Select Eta, full or reduced trim |  |  | 2.7583 | 2.7583 | 2.7583 | 2.7583
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 0.75057 | 0.75057 | 0.75057 | 0.75057
[10 empty] | Selected based on actual Rev |  |  | 0.75057 | 0.75057 | 0.75057 | 0.75057
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 469.9531 | 469.9531 | 469.9531 | 469.9531
[10 empty] | Change from previouse iteration |  |  | 0.0355% | 0.0355% | 0.0355% | 0.0355%
[10 empty] | Assumed C for iterative purposes |  |  | 161.6819 | 161.6819 | 161.6819 | 161.6819
[10 empty] | Valve Reynolds Number | 23 |  | 750.2542 | 750.2542 | 750.2542 | 750.2542
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 2.7577 | 2.7577 | 2.7577 | 2.7577
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 117.608 | 117.608 | 117.608 | 117.608
[10 empty] | Select Eta, full or reduced trim |  |  | 2.7577 | 2.7577 | 2.7577 | 2.7577
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 0.75055 | 0.75055 | 0.75055 | 0.75055
[10 empty] | Selected based on actual Rev |  |  | 0.75055 | 0.75055 | 0.75055 | 0.75055
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 469.9897 | 469.9897 | 469.9897 | 469.9897
[10 empty] | Change from previouse iteration |  |  | 0.007787% | 0.007787% | 0.007787% | 0.007787%
[10 empty] | Assumed C for iterative purposes |  |  | 161.6855 | 161.6855 | 161.6855 | 161.6855
[10 empty] | Valve Reynolds Number | 23 |  | 750.2474 | 750.2474 | 750.2474 | 750.2474
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 2.7576 | 2.7576 | 2.7576 | 2.7576
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 117.6097 | 117.6097 | 117.6097 | 117.6097
[10 empty] | Select Eta, full or reduced trim |  |  | 2.7576 | 2.7576 | 2.7576 | 2.7576
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 0.75055 | 0.75055 | 0.75055 | 0.75055
[10 empty] | Selected based on actual Rev |  |  | 0.75055 | 0.75055 | 0.75055 | 0.75055
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 469.9977 | 469.9977 | 469.9977 | 469.9977
[10 empty] | Change from previouse iteration |  |  | 0.001709% | 0.001709% | 0.001709% | 0.001709%
[10 empty] | Assumed C for iterative purposes |  |  | 161.6862 | 161.6862 | 161.6862 | 161.6862
[10 empty] | Valve Reynolds Number | 23 |  | 750.2459 | 750.2459 | 750.2459 | 750.2459
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 2.7576 | 2.7576 | 2.7576 | 2.7576
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 117.61 | 117.61 | 117.61 | 117.61
[10 empty] | Select Eta, full or reduced trim |  |  | 2.7576 | 2.7576 | 2.7576 | 2.7576
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 0.75055 | 0.75055 | 0.75055 | 0.75055
[10 empty] | Selected based on actual Rev |  |  | 0.75055 | 0.75055 | 0.75055 | 0.75055
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 469.9995 | 469.9995 | 469.9995 | 469.9995
[10 empty] | Change from previouse iteration |  |  | 0.000375% | 0.000375% | 0.000375% | 0.000375%
[10 empty] | Assumed C for iterative purposes |  |  | 161.6864 | 161.6864 | 161.6864 | 161.6864
[10 empty] | Valve Reynolds Number | 23 |  | 750.2455 | 750.2455 | 750.2455 | 750.2455
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 2.7576 | 2.7576 | 2.7576 | 2.7576
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 117.6101 | 117.6101 | 117.6101 | 117.6101
[10 empty] | Select Eta, full or reduced trim |  |  | 2.7576 | 2.7576 | 2.7576 | 2.7576
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 0.75055 | 0.75055 | 0.75055 | 0.75055
[10 empty] | Selected based on actual Rev |  |  | 0.75055 | 0.75055 | 0.75055 | 0.75055
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 469.9999 | 469.9999 | 469.9999 | 469.9999
[10 empty] | Change from previouse iteration |  |  | 8.231e-05% | 8.231e-05% | 8.231e-05% | 8.231e-05%
[10 empty] | Assumed C for iterative purposes |  |  | 161.6864 | 161.6864 | 161.6864 | 161.6864
[10 empty] | Valve Reynolds Number | 23 |  | 750.2455 | 750.2455 | 750.2455 | 750.2455
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 2.7576 | 2.7576 | 2.7576 | 2.7576
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 117.6101 | 117.6101 | 117.6101 | 117.6101
[10 empty] | Select Eta, full or reduced trim |  |  | 2.7576 | 2.7576 | 2.7576 | 2.7576
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 0.75055 | 0.75055 | 0.75055 | 0.75055
[10 empty] | Selected based on actual Rev |  |  | 0.75055 | 0.75055 | 0.75055 | 0.75055
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 470 | 470 | 470 | 470
[10 empty] | Change from previouse iteration |  |  | 1.806e-05% | 1.806e-05% | 1.806e-05% | 1.806e-05%
[10 empty] | Assumed C for iterative purposes |  |  | 161.6865 | 161.6865 | 161.6865 | 161.6865
[10 empty] | Valve Reynolds Number | 23 |  | 750.2454 | 750.2454 | 750.2454 | 750.2454
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 2.7576 | 2.7576 | 2.7576 | 2.7576
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 117.6101 | 117.6101 | 117.6101 | 117.6101
[10 empty] | Select Eta, full or reduced trim |  |  | 2.7576 | 2.7576 | 2.7576 | 2.7576
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 0.75055 | 0.75055 | 0.75055 | 0.75055
[10 empty] | Selected based on actual Rev |  |  | 0.75055 | 0.75055 | 0.75055 | 0.75055
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 470 | 470 | 470 | 470
[10 empty] | Change from previouse iteration |  |  | 3.965e-06% | 3.965e-06% | 3.965e-06% | 3.965e-06%