## Sheet1
CONTROL VALVE SIZING: STEAM or VAPOR |  |  | TAG: | PV123 |  |  |  | Jon Monsen |  | Valve sizing per ISA S75.01.01 2007
[10 empty] | DESCRIPTION OF VARIABLE | Eq | NAME OF VARIABLE | FORMULA
Flow | lbm/h | W | 2295 | 2495 | 2695 | 2895 | Valve type |  | Valve style SPL code | CALCULATED IN COLUMN "S" |  | CALCULATED IN COLUMN "S"
Inlet pressure | psiA | P_1 | 100 | 100 | 100 | 100 | Globe |  | 0 | Pressure drop ratio | 9 | x | 0.25 | 0.25 | 0.25 | 0.25
Inlet temperature | F | T_1 | 100 | 100 | 100 | 100 | Rotary eccentric plug |  | 1 | Ratio of specific heats factor | 11 | F_GAMMA | 1 | 1 | 1 | 1
Pressure drop | psi | DELTA_P | 25 | 25 | 25 | 25 | Segment ball |  | 2 | Absolute temperature |  | T_abs | 560 | 560 | 560 | 560
Density | lbm/ft^3 | RHO | 0.4824 | 0.4824 | 0.4824 | 0.4824 | Butterfly |  | 3
Molecular weight* |  | M | 28.97 | ======> | ======> | ======> | Full ball |  | 4 | WITHOUT REDUCERS
Specific heat ratio |  | GAMMA | 1.4 | ======> | ======> | ======> |  |  |  | Expansion factor | 12 | Y | 0.8366 | 0.8366 | 0.8366 | 0.8366
Choked press drop ratio factor |  | x_T | 0.51 | 0.51 | 0.51 | 0.51 |  |  |  | C Non choked | 5 | C_NonCh | 12.4792 | 13.5667 | 14.6542 | 15.7417
Inlet pipe diameter | inch | D_1 | 2 | ======> | ======> | ======> |  |  |  | C Choked | 5 | C_Ch | 10.9588 | 11.9139 | 12.8689 | 13.8239
Outlet pipe diameter | inch | D_2 | 2 | ======> | ======> | ======> |  |  |  | Choked pressure drop ratio | 10 | CH_x | 0.51 | 0.51 | 0.51 | 0.51
Valve size | inch | d | 1 | ======> | ======> | ======> |  |  |  | Select C Non choked or C choked |  | Select_C_Non_or_C_Ch | 12.4792 | 13.5667 | 14.6542 | 15.7417
Valve style SPL code |  | VSC | 4 | ======> | ======> | ======> |  |  |  | (This is the initial guess for
Pipe wall correction | dB(A) | DeltaLp | -2 | ======> | ======> | ======> |  |  |  | the following iterative calculations)
Required flow coef. (Cv or Kv) | Cv | C_ | 13.3642 | 14.7274 | 16.1508 | 17.6444
Flow calculated from C_ above |  |  | 2295 | 2495 | 2695 | 2895 |  |  |  | WITH REDUCERS
Outlet velocity | Mach |  | 0.27826 | 0.30251 | 0.32676 | 0.35101 |  |  |  | Reducer velocity head coefficients | 18 | ZETA_1 | 0.28125 | ======> | ======> | ======>
Sound pressure level | dB(A) |  | 75.497 | 76.0875 | 76.6485 | 77.1862 |  |  |  |  | 17 | ZETA_B1 | 0.9375 | ======> | ======> | ======>
Selected valve style (VSC) |  |  | Ball | [7 empty] | 19 | ZETA_2 | 0.5625 | ======> | ======> | ======>
[6 empty] | Data input |  |  |  |  | 17 | ZETA_B2 | 0.9375 | ======> | ======> | ======>
[6 empty] | Final results |  |  |  | Sum of velocity head coefficients | 16 | SIGMA_ZETA | 0.84375 | ======> | ======> | ======>
[10 empty] | Sum of upstream velocity head coef |  | SIGMA_ZETA_1 | 1.2188 | ======> | ======> | ======>
Numerical constants | [9 empty] | Beginning of iterative calculation
N_2 | 890 | [8 empty] | Assumed C for iterative purposes |  | C_i | 12.4792 | 13.5667 | 14.6542 | 15.7417
N_5 | 1000 | [8 empty] | Piping geometry factor | 15 | F_P | 0.93346 | 0.92273 | 0.91151 | 0.89987
N_6 | 63.3 | [8 empty] | Choked Pres drop ratio factor with reducers | 22 | x_TP | 0.53364 | 0.5375 | 0.54154 | 0.54575
[10 empty] | Expansion factor | 12 | Y_W_Reducers | 0.84384 | 0.84496 | 0.84612 | 0.84731
FLAG_A | 1 | 1= Inlet Temp entered in F is converted to R in T_abs field | [7 empty] | C Non choked w/ reducers | 5 | C_NonCh_W_Reducers | 13.254 | 14.5573 | 15.896 | 17.2723
|  | 2= Inlet Temp entered in C is coverted to K in T_abs field | [7 empty] | C Choked w/ reducers | 5 | C_Ch_W_Reducers | 11.477 | 12.5769 | 13.7008 | 14.8504
[10 empty] | Choked pressure drop ratio w/ reducers | 10 | CH_x_W_Reducers | 0.53364 | 0.5375 | 0.54154 | 0.54575
[10 empty] | Select C Non choked or C choked |  |  | 13.254 | 14.5573 | 15.896 | 17.2723
FLAG_1 | 1 | 1=flow coef is Cv 2=flow coef is Kv
[10 empty] | Assumed C for iterative purposes |  |  | 13.254 | 14.5573 | 15.896 | 17.2723
FLAG_2 | 1 | 1=psiA, deg F, 2=bar or kPa, Deg C | [7 empty] | Piping geometry factor | 15 |  | 0.92587 | 0.91253 | 0.89819 | 0.88291
FLAG_1 and FLAG_2 only have an effect in the noise calculation | [9 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53637 | 0.54118 | 0.54636 | 0.5519
[10 empty] | Expansion factor | 12 |  | 0.84463 | 0.84601 | 0.84748 | 0.84901
*The Molecular weight entry is only used in the | [9 empty] | C Non choked w/ reducers | 5 |  | 13.3502 | 14.7018 | 16.106 | 17.5689
noise calculation and the Mach number calculation. | [9 empty] | C Choked w/ reducers | 5 |  | 11.5416 | 12.6742 | 13.8426 | 15.0511
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53637 | 0.54118 | 0.54636 | 0.5519
This worksheeet is distributed at no cost on an as-is basis. | [9 empty] | Select C Non choked or C choked |  |  | 13.3502 | 14.7018 | 16.106 | 17.5689
The author assumes no liability for its use.
[10 empty] | Assumed C for iterative purposes |  |  | 13.3502 | 14.7018 | 16.106 | 17.5689
| The cells below (Row 47) detrmine if any input data is missing. | [8 empty] | Piping geometry factor | 15 |  | 0.92491 | 0.91101 | 0.89589 | 0.87956
| If it is, error messages are blanked out of the calculated results. | [8 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53672 | 0.54173 | 0.54719 | 0.55312
| DATA1 | DATA2 | DATA3 | DATA4 | [5 empty] | Expansion factor | 12 |  | 0.84473 | 0.84617 | 0.84771 | 0.84934
| -45800127989.28 | -49791424546.08 | -53782721102.88 | -57774017659.68 | [5 empty] | C Non choked w/ reducers | 5 |  | 13.3624 | 14.7235 | 16.1429 | 17.6289
[10 empty] | C Choked w/ reducers | 5 |  | 11.5499 | 12.6889 | 13.8676 | 15.0918
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53672 | 0.54173 | 0.54719 | 0.55312
[10 empty] | Select C Non choked or C choked |  |  | 13.3624 | 14.7235 | 16.1429 | 17.6289
[10 empty] | Assumed C for iterative purposes |  |  | 13.3624 | 14.7235 | 16.1429 | 17.6289
[10 empty] | Piping geometry factor | 15 |  | 0.92479 | 0.91078 | 0.89548 | 0.87888
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53676 | 0.54181 | 0.54734 | 0.55337
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.84619 | 0.84775 | 0.84941
[10 empty] | C Non choked w/ reducers | 5 |  | 13.364 | 14.7269 | 16.1494 | 17.6412
[10 empty] | C Choked w/ reducers | 5 |  | 11.551 | 12.6912 | 13.872 | 15.1002
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53676 | 0.54181 | 0.54734 | 0.55337
[10 empty] | Select C Non choked or C choked |  |  | 13.364 | 14.7269 | 16.1494 | 17.6412
[10 empty] | Assumed C for iterative purposes |  |  | 13.364 | 14.7269 | 16.1494 | 17.6412
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.89541 | 0.87874
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55342
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1506 | 17.6437
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6915 | 13.8728 | 15.1019
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55342
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1506 | 17.6437
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1506 | 17.6437
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.87871
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6442
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6915 | 13.8729 | 15.1022
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6442
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6442
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6443
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6443
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6443
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6443
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6443
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6443
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Assumed C for iterative purposes |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 |  | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 |  | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | C Non choked w/ reducers | 5 |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | C Choked w/ reducers | 5 |  | 11.5511 | 12.6916 | 13.8729 | 15.1023
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select C Non choked or C choked |  |  | 13.3642 | 14.7274 | 16.1508 | 17.6444
Confirmation that the calculated C will produce the given flow rate
[10 empty] | Final C calculated above |  | Final_Calculated_C | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Piping geometry factor | 15 | Final_F_P | 0.92477 | 0.91074 | 0.8954 | 0.8787
[10 empty] | Presssure drop ratio factor w/reducers | 22 | Final_x_TP | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Expansion factor | 12 | Final_Y_W_Reducers | 0.84475 | 0.8462 | 0.84776 | 0.84942
[10 empty] | Flow Non choked w/ reducers | 7 | Final_Flow_NonCh_W_Reducers | 2295 | 2495 | 2695 | 2895
[10 empty] | Flow Choked w/ reducers | 7 | Final_Flow_Ch_W_Reducers | 2655.2367 | 2895.2298 | 3137.5042 | 3382.2957
[10 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 | Final_CH_x_W_Reducers | 0.53677 | 0.54182 | 0.54737 | 0.55343
[10 empty] | Select flow Non choked or flow choked |  | Calc_Flow_From_Final_ Calc_C | 2295 | 2495 | 2695 | 2895
Aerodynamic noise calculation based on VDMA 24422 - 1979 as presented in the Metso "Flow Control Manual"
[10 empty] | Valve flow capacity in Cv units |  | C_v | 13.3642 | 14.7274 | 16.1508 | 17.6444
[10 empty] | Upstream pressure, P1, in units of psiA |  | P_1_psia | 100 | 100 | 100 | 100
[10 empty] | Upstream temperature in units of degrees R |  | T_1_degR | 560 | 560 | 560 | 560
[10 empty] | Gas density in units lb/ft^3 at std cond (14.7 psiA, 60 F) |  | RHO_n | 0.076423 | ======> | ======> | ======>
VALVE SPECIFIC CORRECTION COEFFICIENT
[10 empty] | For globe valves |  | DeltaLg_0 | 0 | 0 | 0 | 0
[10 empty] | For eccentric rotary plug valves |  | DeltaLg_1 | -1 | -1 | -1 | -1
[10 empty] | For segment ball valves |  | DeltaLg_2 | 2.83 | 2.83 | 2.83 | 2.83
[10 empty] | For butterfly valves |  | DeltaLg_3 | 1.675 | 1.675 | 1.675 | 1.675
[10 empty] | For ball valves |  | DeltaLg_4 | 1.675 | 1.675 | 1.675 | 1.675
[10 empty] | For selected valve based on VSC (Valve Style Code) |  | DeltaLg | 1.675 | 1.675 | 1.675 | 1.675
[10 empty] | P_2 in psiA |  | P_2_psia | 75 | 75 | 75 | 75
[10 empty] | High downstream pressure correction |  | DeltaLp2 | 0 | 0 | 0 | 0
[10 empty] | Calculated Sound Pressure Level (dBA) |  | L_A | 75.497 | 76.0875 | 76.6485 | 77.1862
Valve outlet Mach Number calculation
[10 empty] | Valve nominal size in inches |  | d_in | 1 | ======> | ======> | ======>
[10 empty] | Mass flow converted to lbm/h |  | W_to_lbm_h | 2295 | 2495 | 2695 | 2895
[10 empty] | Density in units of lb/ft^3 |  | RHO_lb_ft3 | 0.4824 | 0.4824 | 0.4824 | 0.4824
[10 empty] | Mass flow in lbm/h converted to scfh |  | lbm_h_to_scfh | 30022.9877 | 32639.3701 | 35255.7525 | 37872.1349
[10 empty] | Valve outlet velocity (Mach Number) |  | MN | 0.27826 | 0.30251 | 0.32676 | 0.35101